# VOLUME 3

# TECHNICAL SPECIFICATIONS

for the Designing project of the reconstruction and extension of the business building B+GF+2,

at Cadastral parcel no. 488/2 Cadastral Municipality Knjazevac in 41 Knjaza Milosa Street

On the basis of the request and the designing project task of the Municipality of Knjazevac – Sports Association of Knjazevac, location conditions, and for purposes of drafting the programme of crossborder cooperation „Interreg – IPA CBC Bulgaria – Serbia“, a designing project documentation has been created. The project includes reconstruction of the existing business building on the first floor, erection of an annexed building part on the north side, as well as building of a new floor (the second floor) within the roof height of the existing building.

Previous condition

On the parcel of the total area of 3,25 ares, during the 20th century, a business building was built, measuring 11,50 x 14,70 m, floor GF+1 (ground floor and first floor), with a basement  occupying approximately a third of the building’s floor base. The narrow side of the building is oriented towards Knjaza Milosa Street; to be more precise, the building line matches the boundary line of the parcel and pavement.

The ground floor and the front side entrance used to house two offices, while the back, north side of the building houses the entrance to the first floor with a prefabricated wooden staircase within the building. These two offices were joined into a single office at the end of the 20th century. The first floor of the building is now used as an office space of the Sports Association of Knjazevac.

The building was built of solid material. The exterior and most of the interior walls on the ground floor were built of 51cm solid brick (old brick format plus mortar), while the first floor walls were built of 35cm solid brick, together with mortar.

The building foundation structure is not visible and cannot be analysed. However, the plinth part of the building, which is visible in the height of 30-50cm, depending on the terrain level, is built of chipped stone, while, supposedly, the foundation was built of broken stone. The basement walls were built of stone blocks with the ceiling of full brick with three vaults. The basement entrance is on the north side of the building.

The inter-floor structure is built of steel „I“ beams and shallow vaults of solid brick. Below the inter-floor structure today there is a lowered coffered ceiling made of gypsum boards, and above it there is a floor consisting of wooden battens, slag infill and the final hardwood floor. The floor construction to the attic is built of wooden beams and „karatavan“ structure, clay and straw infill with reed-plaster ceiling on the bearing construction made of planks.

The double sloped hipped roof slopes at 30 degrees, with the parapet in form of facade walls about 40cm from the end section of the attic and the facade profiled cornice brick. The roof is a wooden rafted structure with tile cladding.

At all angles, as well as in the thirds of the east building part, brick overhangs were built in form of reinforcement („pilaster“) from the foundation level to the profiled facade cornice. The overhangs emphasize the bearing constructive structure of the building.

The building has two balconies. The small balcony is on the front side and the big balcony is in the middle on the back side which canopies the entrance door to the first floor.

The gutters are lying and are positioned on the very edge of the profiled cornice, with four separate downspouts, two on the front and two on the back side of the building.

The fenestration is wooden with classic double framed windows which are painted in oil-based paint, except for the recently installed display windows of the bank which are built of eloxated aluminium with larger glass surface. The interior doors are wooden and solid, and are also painted in oil-based paint.

The net area of the business area on the ground floor which is used by offices amounts to approximately 120m2, while the business area on the first floor is 132m2 and the basement area is around 38m2.

Reconstruction and extension

A precondition for the reconstruction and extension of the building is demolition of all subsequently extended auxilliary buildings from the north side which were built during the years after the building had been erected, as well as dismantling of the complete wooden structure of the roof with the wooden beams and „karatavan“ structure. Besides these, some of the 18cm thick partition walls and both balconies are to be demolished, all the windows and doors are to be dismantled, the hardwood floor is to be removed and plaster is to be stripped off the interior walls on the first floor. Also, all sanitary equipment is to be dismantled, as well as the mobile office equipment and furniture.

The reconstruction of the existing building implies building a new semi-prefabricated reinforced concrete inter-floor „fert“ slab structure which lowers the light height to 3,00 m, measured from the final floor construction. The reconstruction also implies building new reinforced concrete ring beams by chase cutting onto the interior side of the facade walls and over all interior bearing walls. The existing staircase opening in the inter-floor construction, measuring 95 x 250cm, is to be closed with full reinforced concrete floor structure.

According to the new organization scheme on the first floor, it is necessary to build partition walls in the sanitary facility of 12cm thick hollow clay block and to erect 10cm thick gypsum board walls.

The existing and new walls including the floor ceiling construction, are to be plastered with flexible mortar. Prior to replacing the floors with modern floor types, the existing battens are to be replaced with water-resistant boards, a floating layer of 2cm Styrodur, 4cm thick cement screed with light reinforcement and, finally, homogeneous vinyl floor (that is, ceramics in the sanitary facilities).

The extension of the building is to be done in two ways:

-	building an annex on the north side of the existing building, new staircase and lift within the dimensions of 2,85 + 1,60 m x 7,30 m

-	building a new floor section within the height of the existing building, with an annex in form of the staircase and lift area

The building is built in the second climate zone and eighth seismic zone.

After the building had undergone an expert engineering inspection, it was concluded that there is no need of reinforcing the foundation and that the new reinforced concrete floor construction and complete new floor can be built. No cracks or foundation subsidence were observed.

The annexed building part will house a reinforced concrete staircase from the ground floor to the second floor, as well as an extended area for the lift for people with disabilities. The canopied entrance stair landing is oriented towards east with a slanted gate for access for people with disabilities. Above the stair landing, of same dimensions, is a terrace on the floor with access from the staircase area.

Extension building of the second floor is to be done within the height of the ridge of the existing roof construction and the unchanged height of the facade walls cornice. The new floor has a smaller surface area than the base and a full room height of 2,80 m despite the fact that it resembles an attic.

The new walls of the second floor and the annexed building are to be built of 25cm thick gas concrete block with vertical and horizontal reinforced concrete ring beams and partition walls of 12cm thick hollow clay blocks.

Above the offices, meeting rooms and most of the hallway, a lowered gypsum board ceiling is to be positioned at the height of 2,80 m. Above the sanitary facility and tea-kitchen the same kind of ceiling will slope until the minimum height of 2,40 m. Above the staircase and the lift, the ceiling will follow the roof rafters inclination. The flat roof part has previously laid timber battens and then a lowered gypsum board ceiling is to be assembled, which will be hung on the metal galvanized substructure. The designing project envisages positioning of thermal insulation of mineral wool over the gypsum board ceiling.

The wooden roof is clad in 15mm thick OSB (Oriented strand boards)  panels, the roof foil, timber battens and reverse battens, and, finally, interlocking clay tiles.

The frontal reinforced concrete ring beam of the elevations of the second floor walls is profiled in the shape of the existing cornice with the lying gutter on its edge. New profiled jambs are to be made in the same shape above the windows of the first floor.

All interior walls are to be plastered with flexible mortar and rendered in acryllic paint, except for the walls of the sanitary facility and tea-kitchen which are to be covered in ceramic tiles.

Bitumenuos insulation, screed and on top the granite ceramics, are to be laid over the concrete slab construction of the entrance area and staircase. Above the new concrete slab construction on the second floor, 5 cm Styrodur, PE foil, 4cm cement screed with light reinforcement and on top laminate, or, in the sanitary facility, ceramics, are to be positioned.

The existing and new facade walls are to be covered in 10cm thick stone wool facade and rendered in plastic plaster.

All sheet-metal structures on the building: gutters, downspouts, flashings, drip caps are to be made of galvanized sheet metal.

The facade fenestration with windows, front door and light well around the lift shaft is to be made of thermal barrier eloxated aluminium profiles with thermal glazing. The interior doors are to be made of aluminium or PVC.

The entrance door from the staircase area towards rooms on the first and second floor are 30 minutes fire-resisting and fireproof, according to the fire protection regulations.

The terrace fence on the floor is built of hollow horizontal aluminium profiles and appropriate two-wall aluminium poles. The fence around the gate for people with disabilities is built of hollow aluminium profiles with handrails in two levels, at 70 and 90cm.

The panoramic-glazed hydraulic lift has a 110x 140cm cabin and is designed in accordance with the needs of people with disabilities.

The reconstructed and extended building, in terms of its infrastructure, is to be connected to all existing networks of the existing building: the water supply, sewerage, electric distribution network, postal and telephone network and town heating system.

NUMERIC DOCUMENTATION

Overview of the building areas with their functions and numbers of functional units with necessary public utility capacities

BASEMENT:

- ARCHIVES ........................................................      38,20 m2

GROUND FLOOR:

- ENTRANCE STAIR LANDING .........................     6,70 m2

- STAIRCASE AREA WITH LIFT .......................    22,00 m2

- STORAGE ROOM ..............................................      6,65 m2

________________________________________________________

TOTAL NET AREA:                 35,35 m2 + (office 119,60 m2)

GROSS EXTENDED CONSTRUCTION AREA OF THE FLOOR PLAN:  194,50 m2

FIRST FLOOR (DIAGNOSTIC CENTRE):

- STAIRCASE WITH LIFT............................................  22,00 m²

- TERRACE (LOGGIA).................................................    6,70 m²

- WAITING ROOM.......................................................     7,80 m²

- HALLWAY..................................................................   14,55 m²

- PHOTOMETRIC INSTRUMENT...............................   16,35 m²

- ANTHROPOMETRIC MEASUREMENT ROOM.....   13,70 m²

- CORRECTION HALL ................................................   50,10 m²

- DRESSING ROOMS – men’s and women’s...............   18,30 m²

- SANITARY FACILITY - men’s and women’s...........     4,75 m²

- WC FOR PEOPLE WITH DISABILITIES.................     5,10 m²

- HYGIENE STORAGE ROOM....................................     1,70 m²

_______________________________________

TOTAL NET AREA: 	                   161,05 m2

GROSS EXTENDED CONSTRUCTION AREA OF THE FIRST FLOOR:  194,50 m2

SECOND FLOOR (SPORTS men’s and women’s...ASSOCIATION OFFICES):

- STAIRCASE WITH LIFT...........................................   22,00 m²

- HALLWAY  ...............................................................   12,70 m²

- OFFICE 1   ..................................................................   18,20 m²

- OFFICE 2  ...................................................................   13,95 m²

- MEETING HALL  ......................................................   19,00 m²

- SANITARY FACILITY - men’s and women’s...........    5,60 m²

- SHOWER-BATHROOM ............................................    6,25 m²

- TEA KITCHEN  ..........................................................    3,80 m²

________________________________________

TOTAL NET AREA: 		    101,50 m2

TOTAL NET AREA OF THE BUILDING:       336,10 m2 (without office areas)

GROSS EXTENDED CONSTRUCTION AREA OF THE SECOND FLOOR:         123,45 m2

GROSS EXTENDED CONSTRUCTION AREA OF THE BUILDING B+GF+2:     575,85 m2

RECONSTRUCTED AND EXTENDED BUSINESS BUILDING B+GF+2 IS A BUILDING WITH TWO FUNCTIONAL UNITS; GROUND FLOOR OFFICE AND DIAGNOSTIC CENTRE ON THE FIRST FLOOR  WITH SPORTS ASSOCIATION OFFICES ON THE SECOND FLOOR

IMPORTANT:

All works must be implemented in accordance with investment design and corresponding standarts.

In case that in investment design - explanatory notes, bills of quantities, drawings, specifications, and everywhere in the documentation for tendering are set specific brand/mark, model, type, standard materials and products to be considered that whereas and equivalent.

The Contracting Authority does not require specific make, model, type, standard materials and products that will be in the works as long as you comply with the specifications of the designers and the essential requirements for building works.

Annex 1 – Bill of quantities

Annex 1

BILL OF QUANTITIES

| DESCRIPTION | UNIT | QUANTITY |  |
| --- | --- | --- | --- |
| 1. DEMOLITION WORKS: |  |  |  |
| 1.Dismantling of tiles, planks and wooden roof structure a multi-level and auxiliary building with the removal of the material to a place outside of the settlement determined by the investor. Payoff per m2. | m2 | 193,00 |  |
| 2.The demolition of interior walls of solid bricks chimney above attic and parts of the outer walls of multi-level and auxiliary building openings, for windows, with removal of the material to a landfill outside of the settlement. Payoff per m3. | m3 | 38,00 |  |
| 3.Demolition of all entry concrete stairs and terrace with the removal and transport of the rubble on a landfill outside of the settlement. Payoff per m3 | m3 | 6,00 |  |
| 4.Demolition of all existing floors in building on the floor all the way to the ceiling made of solid brick, with removal and transportation of the material to the landfill. Payoff per m2. | m3 | 130,00 |  |
| 5.Demolition of the existing attic, the joists and ceiling the removal and transport of the rubble to the landfill. | m2 | 130,00 |  |
| 6.Breaking up the concrete floor of theauxiliary building and the part of the stairs leading to the basemen with pneumatic hammer and sledgehammer, with the removal and transport of the rubble to the landfill. | m2 | 28,00 |  |
| 7.Removal of the dilapidated plaster from the facades the use of scaffolding. Payoff per m2. (Estimated at 30% of the facade).. | m2 | 140,00 |  |
| 8.Completely removal of plaster from the interior walls of floor-to-brick, floor to ceiling, with the use of light scaffolding transport of the materials to the dump outside of the settlement. Payoff per m2. | m2 | 450,00 |  |
| 9.Complete dismantling-extracting of the existing timber Carpentry - doors and windows from the floor and auxiliary building, as well as storage and transport to the place by the investor. Payoff per piece. | windows pieces | 15,00 |  |
|  | doors pieces | 18,00 |  |
| 10.Dismantling of the existing prefabricated, wooden stairs to the first floor with the removal and transportof the rubble to landfill outside of the settlement. Payoff per m2 | m2 | 7,50 |  |
| 11.Dismantling of the entire sheet metal with of the objectmade of galvanized steel, with removal and transportation of the material of the material to a landfill outside of the settlement. as a lump sump. | lump sum | 1,00 |  |
| 12.Dismantling of the existing fence beside the inside stairs and the terrace, with a storage place determined by the investor Payoff per meters | m | 17,00 |  |
| 2. GROUND WORKS: |  |  |  |
| 1.Wide digging of category III, using machinery and, for the elevator shaft, with the transport of the land to the dump outside of the settlement Payoff per m3.. | m3 | 6,80 |  |
| 2.Digging of the land of category III, manually, to the depth of 2.00 m for the core tapes and footings, with the transport of the land to landfill outside of the settlement Payoff per m3. | m3 | 7,50 |  |
| 3.Filling, spreading and compacting of the land from the excavation, around foundations and foundation walls in layers of 20 cm until complete compaction with manual compactors Payoff per m3. | m3 | 3,80 |  |
| 4. Delivery, filling and ramming roadbase layer of the gravel under the foundation and floor, 10 cm thickness Payoff per m3 | m3 | 4,50 |  |
| 3. MASONRY: |  |  |  |
| 1.Masonry of exterior and interior walls with the gas concrete block block, 25 cm thick, on adhesive Payoff per m3. | m3 |  | 36,00 |
| 2.Masonry of the partition walls with the gas concrete block blocks 12 cm thick, on adhesive Payoff per m2 | m2 |  | 104,60 |
| 3.Masonry of the partition wall thickness of 7 cm from the "three-channel" on edge with simultaneous production of cerclage in the height the lintel and armature ± 2 Ø 10. Payoff per m2 | m2 |  | 5,00 |
| 4.Production of drywall plasterboard on the substructure from galvanized profiles d = 10 cm (1 + 8 + 1) with a 6 cm mineral wool Payoff per m², with bandaged joints, smoothing and corner rails | m2 |  | 34,00 |
| 5.Production of suspended ceiling made of plasterboard, water-repellent slabs on galvanized, hanging with substructure lowering the height on 20 cm below the ceiling of the bathroom. Payoff per m²,tila. Claculation upon m², with fulfilment of joints, ith bandaged joints, and corner rails. | m2 |  | 16,00 |
| 6.Production of suspended ceiling in office, dining room and the kitchen made of standard plasterboard slabs on galvanized substructure with lowering of the height on 20 cm below the ceiling. Payoff per m², with bandaged joints smoothing and corner rails | m2 |  | 86,00 |
| 7.Supply and installation of prefabricated sanitary partitions for WC with two doors, made from laminated panel thickness 13 mm, in a frame made of stainless steel, with adjustable feet and stainless steel of the “L”profile and attachment to the wall. Payoff per m2 | m2 |  | 11,00 |
| 8. Plastering interior walls with lime mortar1:2:6. (Extensions and on the existing the floor)Payoff per m2 | m,2 |  | 890,00 |
| 9.Plastering the new fert construction with the extended mortar 1: 2: 6 . Payoff per m2 | m2 |  | 168,00 |
| 10.Plastering of the outer walls with the extended mortar 1: 3: 9 in one procurement as basis for thermal isolation(new walls, and 30% of the existing walls). Payoff per m2, together with the installation of scaffolding. | m2 |  | 165,00 |
| 11.Plastering of the bottom side of the staircase slabs, visible A.B. beams and concrete slabs below, with the extended mortar 1: 2: 6 while previously dousing the whole surface with cement milk. Payoff per m2 | m2 |  | 42,00 |
| 12.Smoothing plaster walls and ceilings with polyfix. Payoff per m2 | m2 |  | 1.060,00 |
| 4. CONCRETE AND ARM.CON.WORKS: |  |  |  |
| 1.Concreting treading of the strip foundations, foundations footings, Fundamental cerclage, foundation beams and the elevator pit made of A.C. concrete MB 20. Payoff per m3 | m3 | 8,20 |  |
| 2.Concreting A.B vertical, horizontal cerclage, square pillars, lintels and of the lintel made of MB 20 in the required sheetings. Payoff per m3. | m3 | 18,00 |  |
| 3.Concreting interior A.B. stairs in the crank platesystem crank plate d = 12 cm from MB 20 in the required smooth sheetings. Payoff per m3 | m3 | 3,80 |  |
| 4. Concreting of the entry stairs, ramps and landings on field of compacted concrete MB 20 in smooth sheetings. | m3 | 1,90 |  |
| 5. Concreting AB the ceiling of the type "fert" - 16, with lightly reinforced slab thickness 4 -5 cm Payoff per m2 | m3 | 154,00 |  |
| 6. Concreting the console panel of the terrace, 10 cm thickness made of the MB 20 in required smooth sheetings.Payoff per m2 | m3 | 11,20 |  |
| 7. Concreting the base slab of the ground floor, reinforced network thickness of 10 cm made of MB 20. Payoff per m2. | m2 | 22,00 |  |
| 8. Concreting rabicated cement screed for the ground floor and first floor (via thermal isolation),4 cm thick Payoff per m2 | m2 | 190,00 |  |
| 9. Pavement thickness of 10 cm, with dilatation fugues and their filled fug. mass made of MB 20.Payoff per m2. | m2 | 22,00 |  |
| 5.REINFORCEMENT WORK: |  |  |  |
| 1.Supply, straightening, cutting, bending and bondingarmature all in accordance with the static calculation and the detail of armature. Payoff per kg. | kg | 4.600,00 |  |
| 6. ISOLATION WORKS: |  |  |  |
| 1. Development of hydro-isolation under the ground floor made of bitumen board with sealed flaps. Prior to this, along the walls realize grooves, and then isolation in the height of 10 cm. Payoff per m2. | m2 | 42,00 |  |
| 2. Production of thermal isolation of the ground floor with "styrodur", thickness of 5 cm, with the laying of protective PE foil Payoff per m2 | m2 | 22,00 |  |
| 3. Production of floating layer for the ground of the the floor of "styrodur"”,2 cm thick with the laying of protective PE foil.. Payoff per m2. | m2 | 145,00 |  |
| 4. Production of thermal isolation to the attic through suspended ceiling of one layer of semi-solid rock wool 12 cm thick and one layer of glass wool 12 cm thickPayoff per m2, together with a vapor barrier, PVC foil. | m2 | 120,00 |  |
| 5. Production of thermal facade, as well as flashings around mansard roof hard-pressed rockwool, 10 cm thickness with overcoating for the plaster and anchoring plastic anchors, with mesh settingglue and finished with fine-grained plastic with fine-grained plastic mortar or teraplast | m2 | 525,00 |  |
| 6. Supply and installation of vapor-permeable roofing foils overlapping joints over the surface with water-repellent slabs. Payoff per m2, without the surface. | m2 | 140,00 |  |
| 7. JOINERY WORK: |  |  |  |
| 1. Supply and installation, facade joinery in PVC aluminum tone windows with multi-chamber profiles and reinforced with galvanized surface all glazed with thermopane glass 4 + 12 + 4 mm all in accordance with the scheme joinery. Payoff per piece. | 70/80 | 5,00 |  |
|  | 100/200 | 6,00 |  |
|  | 11/200 | 1,00 |  |
|  | 100/165 | 4,00 |  |
|  | 135/415 | 1,00 |  |
|  | 183/420 | 3,00 |  |
|  | 183/315 | 3,00 |  |
|  | 183/252 | 3,00 |  |
|  | 285/210 | 1,00 |  |
|  | 285/190 | 1,00 |  |
|  | 225/165 | 1,00 |  |
|  | 225/300 | 1,00 |  |
|  | 115/70 | 1,00 |  |
| 2. Supply and installation of PVC in aluminum tone, glazed entrance, double doors with lights above them with multi-chamber profiles and reinforcement of galvanized surface with the necessary fittings and Elzett-type lock. Payoff per pcs.. | 285/210 | 1,00 |  |
|  | 285/210 | 1,00 |  |
| 3.а Production and installation of steel glazed interior double doors, single glazed fire resistant glass fire resistance of 30 min with the necessary fitting. Payoff per pcs, in the tone of aluminum. | 180/295 | 1,00 |  |
|  | 150/240 | 1,00 |  |
| 3.b Production and installation of steel interior double doors, fire resistant of 30 min with the necessary fitting. Payoff per pcs, in the tone of aluminum. | 91/210 | 1.00 |  |
|  | 95/210 | 1.00 |  |
| 4. Supply and installation of interior, single wing PVC doors, with single-chamber profiles and reinforced galvanized surface supplied with the Elzett-type lock nd standard hinges. Doors with light bulb above with single glass d = 4 mm. Payoff per pcs. in aluminum tone . | 71/210 | 2,00 |  |
|  | 81/210 | 3,00 |  |
|  | 101/210 | 2,00 |  |
|  | 110/210 | 2,00 |  |
|  | 90/210 | 1,00 |  |
|  | 71/280 | 2,00 |  |
|  | 71/300 | 2,00 |  |
|  | 91/280 | 5,00 |  |
|  | 91/300 | 3,00 |  |
| 5. Production and installation of interior glass partitions PVC with doors and fixed, single glazed light bulb above equipped with the necessary fittings and Elzett-type lock. Payoff per pcs, in the tone of aluminum. | 255/300 | 1,00 |  |
| 8. CARPENTRY AND ROOF WORKS: |  |  |  |
| 1. Production of wooden roof structure from cut fir construction, consisting of rafters, “venčanica”, “uvalnica” “grebenjača”, the ridge, columns, struts, and the roof battens pliers, according to the dimensions of the structural analysis.Payoff per m3, of the horizontal projection of the roof. | the roofs slope 30 m2 | 198,00 |  |
|  | mansard roof 90 m2 | 16,00 |  |
| 2. Roof battens fixing of the roof structure with battens and counter battens mension. 3/5 cm. Payoff per m2 of the projection of the roof aslope | m2 | 245,00 |  |
| 3. Setting the roof with water repellant or "OSB" slabs18mm thick. Payoff per m2, of aslope projections. | m2 | 245,00 |  |
| 4. Covering the roof with curved tiles with ventilation tiles closer to the ridge and tiles - snow stops closer to the roof and gutters. Payoff per m2, of aslope projections of the roof | m2 | 245,00 |  |
| 5. Covering the ridge and ridge caps (guttering) by type of tile, with all fasteners for dry mounting according to manufacturer's instructions.Payoff per m. | m2 | 86,00 |  |
| 9.TINSMITHING WORKS: |  |  |  |
| 1. Design and installation of horizontal, gutters, of galvanized plate d = 0.55 mm, rectangular cross section,14 cm wide, RŠ. 35 cm Payoff per m. | m | 74,00 |  |
| 2. Design and installation of the substrate sheet metal from the eaves to below from the eaves to below tiles, galvanized steel RS 25 cm. Payoff per m | m | 74,00 |  |
| 3. Design and installation of vertical drain downpipes,galvanized plate d = 0.55 mm, circular cross-section, Ø 12 cm, RS 40 cm. Payoff per m ' | m | 62,00 |  |
| 4. Flashing roof valleys and the attic of galvanized sheet = 0.55 mm, the RS 50 cm. Payoff per m '’. | m | 66,00 |  |
| 5. Making a canopy on the terrace of galvanized steel d = 0.55 mm, R 20 cm. Payoff per m ' | m | 5,40 |  |
| 6. Flashing sills of all windows, galvanized plate d = 0.55 mm, RS 25 cm. Payoff per m. | m | 17,00 |  |
| 7. Flashing the edge of mansard roof (weather strip)With galvanized tin plates d = 0.55 mm, Rs 20 cm. Payoff per m . | m | 26,00 |  |
| 10. FLOOR LAYING WORKS: |  |  |  |
| 1. Lining the walls of sanitary facilities and kitchenwith ceramic tiles of homemade production optional on the adhesive. Payoff per m2 | m2 | 140,00 |  |
| 2.Covering the floor of sanitary facilities, halls, rooms and stairs with floor tiles, granite-slip tiles , Laser-cut without fugue dimensions and colors are to be chosen by the designer or supervisory authority. Payoff per m2. | m2 | 110,00 |  |
| 3.Creating a plinth next to the walls of the rooms that do not have ceramics on the wall but have it on the floor, to be made of floor ceramics height 10 cm, on the adhesive. Payoff per m '. | m | 46,00 |  |
| 4. Supply and bonding homogeneous vinyl floor wear out category "P" and, the weight of 2.80 kg / m2 colors of choice, with welded joints and patching near the walls. Payoff per m2 | m2 | 134,00 |  |
| 5. Supply and installation of laminate of choice , firmness "32"with appropriate garnish near the wall. Payoff per m2. | m2 | 52,00 |  |
| 6. Supply and installation of ribbed rubber mat or from coconut at the base of the recess near the entrance dimension.80/140 cm. Payoff per pcs. | pcs | 1,00 |  |
| 11. DECORATORS FACADE WORKS: |  |  |  |
| 1. Treatment of plaster and smoothing interior walls using acrylics colors of full dispersion in the color of choice (with deduction of the surfaces under the potterry ). Payoff per m2. | m2 | 750,00 |  |
| 2.Painting and smoothing all of the white plastered ceilings using whiteacrylics colour. Payoff per m2 | m2 | 168,00 |  |
| 3. Treatment of of visible concrete surfaces on the façade, roof, cantilevered slab, the underside of the stair boards with facade paint in the color chosen by the designer or supervisory authorities. Payoff per m2. | m2 | 42,00 |  |
| 4. Treatment of existing stone plinth re-grouting (If necessary) with cement mortar and coating with silicone. Payoff per m2. | m2 | 22,00 |  |
| 12. VARIOUS WORKS: |  |  |  |
| 1. Production of tubular fence for the terrace above the entrance made of aluminum profiles, anodizing in the color of joinery. Payoff per m '. | m | 5,30 |  |
| 2.Production of fences for the internal stairway made of anodized aluminum, construction of choice of the supervisory authority. Payoff per m ' | m | 12,50 |  |
| 3.Making double-sided fence railings ramps for disabled people from two rows of tubes made of anodized aluminum in accordance with the ordinance for disabled persons. Payoff per m '. | m | 6,00 |  |
| 4.The acquisition or production of two concrete flower pots according to the dimensions in the project on the landing entrance Payoff per pcs. | pcs | 2,00 |  |
| 13. HYDRAULIC PANORAMIC LIFT: |  |  |  |
| 1.Supply and installation of the hydraulic passenger lift of the panoramic type, without a special machine room, for the transport of disabled persons, the cabin 110 x 140 cm with automatic door, complete with all the equipment for installation. Payoff per pcs. | pcs | 1,00 |  |
| 14. INSTALATION OF HEATING: |  |  |  |
| 1.Gain body steel panel radiators, complete with support and fixing elements for mounting on the wall type22, height 600mm | 22-600/1200 | 2,00 |  |
|  | 22-600/1000 | 2,00 |  |
|  | 22-600/800 | 13,00 |  |
|  | 22-600/600 | 2,00 |  |
|  | 22-600/400 | 5,00 |  |
| 2.Radiators cap R1/2" | pcs | 24,00 |  |
| 3.Radiator air vent valve R1/2" | pcs | 24,00 |  |
| 4. Thermostatic valves standard TS-90 with internal threads and sealing konisnim connection for heating body complete with thermostatic head | pcs | 24,00 |  |
| 5.Radiators balance valve - return valves flat shape dim. 1/2 Radiator connection with cone. Universal models with special sockets for threaded pipes, compression adapters. | pcs | 24,00 |  |
| 6.Ball valve - threaded connections, complete with dump valves, clamping sealant, the following dimensions: | DN25 | 2,00 |  |
|  | DN40 | 2,00 |  |
| 7.Divorce pipe network- Copper semi-hard pipes SRPS C.D5.500 | Cu Ø40x1.5mm / m | 25,00 |  |
|  | Cu Ø35x1.0mm /m | 30,00 |  |
|  | Cu Ø28x1.0mm /m | 45,00 |  |
|  | Cu Ø22x1.0mm /m | 35,00 |  |
|  | Cu Ø18x1.0mm /m | 40,00 |  |
|  | Cu Ø15x1.0mm /m | 110,00 |  |
| 8.Consumables for welding and assembling pipes, fittings carrier, supports, clamps ... 30% of the positions 14.1 |  | 0,30 |  |
| 15.AIR CONDITIONING INSTALLATION: |  |  |  |
| 1.Supply and erection of single split of air conditioners Cooling: 12000 btu / h (3500W) Heating 13000 BTU / h (3800W) Power supply: 220-240V, 50Hz, 1Ph Power input: Cooling: 1090 W, Heating: 1050 W Current consumption: Cooling: 5.0 / Heating: 4.8 Performance: EER (W / W) 3.21 COP (W / W): 3.61 Dimensions indoor unit (WxHxD): 80 x 29 x 18.6 cm / 10 kg Dimensions outdoor unit (WxHxD): 70 x 54 x 25.5 cm / 30 kg, complete with material for suspension and carrying elements and to connect up to 3m in length. | pcs | 8,00 |  |
| 16. PREPARATORY FINISHING WORK OF HEATING AND AIR-CONDITIONING: |  |  |  |
| 1.Preparatory works including Introducing the facility to perform, the internal transport of materials on site, material storage, construction site security, route marking and location for installation cevovovda and equipment, introduction of assembling a group to work, coordination of the project with the situation at the facility, 4% of the total investment |  | 0,04 |  |
| 2.Completed works involving Performing and visual quality control of welds, flush installation, trial tests (hot and cold test) and filling up water installations performed works and investment documentation and preparation and delivery of the project executed state, 3% of the total investment. |  | 0,03 |  |
| 17.INSTALLATIONS OF SEWAGE NETWORK: |  |  |  |
| 1. Procurement, transport and assembly of PVC sewerage pipes with socket for street and domestic sewage, I class.Connecting pipes with rubber seal with the administration of fittings. Assembly of pipes which are laid in the ground should be performed on the previously prepared subgrade of fine sand d = 10 cm. Pipes in the land will be protected by a layer of sand 10 + D + 10 cm in the full profile of the trench.After the assembling is finished and testing the water permeability trench should be filled with the manual compactor in layers of 20 cm. Inside the building, and above the ground, pipes are installed visibly anchored and hung for the walls, ceilings and other parts of the building, with the previous perforatingo of the opening for the passage of pipes through the foundation, walls and floor structures. The price includes all demolition, all openings, clamps, hanger with all the necessary scaffolding fittings. Payoff per meter of the 'finished with sewage with labor and material. | PVC KK Ø50 mm | 5,00 |  |
|  | PVC KK Ø75 mm | 17,00 |  |
|  | PVC KK Ø110 mm | 25,00 |  |
| 2.Supply, transport and installation of PVC floor siphons with nickel grid. Payoff per built unit. | pcs | 6,00 |  |
| 3.Supply, transport and installation of PVC ventilation head - caps on the ends of sewage verticals above the roof. The penetration through the roof is to be processed so that it is waterproofing. Payoff per piece of ventilation caps installed . | PVC KK Ø150 mm | 1,00 |  |
|  | PVC KK Ø120 mm | 1,00 |  |
| 4.Testing carried out on the sewage network on water permeability of compounds and control of performed downs pipes inside the building.During testings of the water permeability the network must be partially exposed. Testing of the network is to be perform piece by pieceThe openings are to be sealed, except for the highest altitude ones, and network is to be filled with water.Under the given pressure the network is to held for at least 3 hours.Perform an examination and all the places that are leaking are to be marked. Drain off the water and remove all malfunctions. Repeat the testing.During this time theremust not be any water leakage in the investigated part of the sewerage network.Only after successful completion of the testing can the grooves and channels be closed and trenches filled.. Payoff per meter of the 'successful testing of the sewage network. | m' | 47,00 |  |
| 18.INSTALLATION OF WATER SUPPLY NETWORKS: |  |  |  |
| 1.Produce internal water supply from polypropylene PP pipes, all in accordance with the approved project, the general description and instructions of the supervisory authority. Position includes: all the material used with wastage, preparatory- finishing work, the transfer of materials, scaffolding installation is needed for mounting the water supply network under the ceiling structure, measuring, puncturing of the opening through walls and floor construction, mounting clamps, hooks an brackets, making grooves in the wall for laying pipes, pipe inspection, cutting of pipes, connecting pipes, wrapping pipes in the walls with the protective tape, straightening, giving falls, inspection of lines and temporarily closing off the opening in order to examine the test pressure of 12 bar. When installing water supply make sure that the rosette valves and batteries are completely flat with the final surface of the wall. Chiselling for installation and passage pipe is to be done carefully, rubble is to be taken to your city dump , . The price includes the examination of the network to test pressure and for closing the plackets around verticals. Payoff per meters 'of mounted pipes. | PP DN20/Ø15 mm, NP20 | 30,00 |  |
|  | PP DN25/Ø20 mm, NP20 | 12,00 |  |
| 2.Supply and installation of PP Angular gate valve with nickel handle and rosette "EK" valve - cistern connection. Calculation per piece. | Ø1/2" - Ø1/2" | 6,00 |  |
| 3.Supply and installation of PP Angular gate valve with nickel handle and rosette. Installation under the sink. Calculation per piece. | Ø1/2" - Ø3/8" | 8 × |  |
| 4.Supply and installation of PP flat gate valve with nickel plated cap and rosette. The valve is to set on the branches below the boiler and shower. | Ø15 mm | 4,00 |  |
| 5.Supply and installation of PP globe valve with a rosette. The valve is to be set at the beginning of each branch of the bathrooms. Calculation per piece. | Ø20 mm | 3,00 |  |
| 6.Rinsing and disinfection of water supply performed in accordance with applicable regulations. Before putting the network into exploitation the Attest from sanitary services on the quality of drinking water must be obtained. Pay off as a lump sum. | LUMP SUM |  |  |
| 19.INSTALLATION OF FIRE WATER SUPPLY: |  |  |  |
| 1.Reconstruction of the existing water supply connection. Requires a new connector diameter Ø65 mm. Payoff per pcs. | pcs | 1,00 |  |
| 2.Mechanical digging of trench for water supply, III, depth 0 - 2 m, width. Excavation is to be carried out according to the project and given elevations. The sides should be properly cut and the bottom leveled. The excavated earth is to be thrown away from the trench. After completing the works the excess land is to be loaded onto a truck and taken to a dedicated landfill. Payoff per m³ of finished excavation. | m3 | 3,00 |  |
| 3.Procurement, transport and sand filling in the canal trench and around the manhole and pit for the filling under, around and above the sewer pipes in a layer of 10 + D + 10 cm. Payoff per m³ of embedded sand. | m3 | 1,00 |  |
| 4.Backfilling of the excavated canal trench with the excavation material in layers of 20 - 25 cm. The first layer of soil thickness of 1.0 meters above the upper edge of the pipe tamp carefully with a hand-held beater. The rest of the trench is to be compacted by a machine until a compression of 150 kg / cm2 is achieved. Payoff per m³ of buried trench. | m3 | 3,00 |  |
| 5.Procurement, transport and assembly of steel - galvanized pipes. The working pressure of these tubes is 10 bars. Connecting pipes using the fittings. The price includes all chiselling, hole punching, hole patching, clamps, bitumen coatings, protection with jute, as well as dyeing visibly guided tube. Payoff per meters '. | Ø50 mm | 3,20 |  |
|  | Ø65mm | 12,00 |  |
| 6.Supply, transport and assembly of permeable brass valve with wheel to close the drain valve. Payoff per pcs. | Ø65 mm | 1,00 |  |
| 7.Supply, transport and assembly brass irrecoverable valves. Payoff per pcs. | Ø65 mm | 1,00 |  |
| 8.Procurement, transport and assembly of the wall fire hydrant Ø52 mm. In the locker of the following size 54 x 54 x 15 cm are placed: valve Ø52 mm, "Trevira" hose length of 15 meters 'and the corresponding nozzles. All items have a "Štorc" connectors. Payoff per pcs. | pcs | 3,00 |  |
| 9.Supply and installation of water meters with Voltman vertical turbine for water. Maximum water temperature is +30 C, nominal pressure NP10 class A. Set two leaky valves aswell, one of which has a discharge pipe and a suitable fitting. Payoff per pcs. | connection Ø50 mm | 1,00 |  |
| 10.Testing performed on the water supply on hydraulic pressure in accordance with applicable regulations. Payoff per meters '. | m' | 15,00 |  |
| 11.Testing of performed fire hydrants on hydraulic pressure in accordance with applicable regulations and providing confirmation of their examination Payoff per pcs. | pcs | 2,00 |  |
| 12.Rinsing and disinfection of the water supply system carried out in accordance with applicable regulations, as well as obtaining the necessary documentation of performed action. Payoff per meters '. | m' | 13,00 |  |
| 20. SANITARY FACILITIES AND ACCESSORIES: |  |  |  |
| 1.Procure, mount and assemble by regulation with the sewer and water network a complete toilet bowl with the following elements:1. Ceramic toilet bowl with lead cuff compound to the sewage network, two brass screws with plastic inserts between screws and cups, as well as a rubber pad between the cup and the floor.2.The lid for toilet bowl made of hard plastic with the necessary screws for connecting with the toilet bowl3. Noise-free PVC cistern. The cistern is to be set at a height of 1.0 m from the floor to the two steel hooks fastened to the wall using anchors.4. Flexible connection hose for cistern made of PVC, 400 mm.5. Plastic tube F 40 mm for thecompound of cisterns and toilet bowl for high mounting and wall mounting with all necessary fittings and rubber gaskets and cuff for the compound pipe and two plastic bowls and clamps for fastening to the wall.Completely built toilet bowl is being paid per piece of the mounted toilet bowl. | Simplon | 6,00 |  |
| 2.Supply and installation of a set of sinks, consisting of the following elements: 1. Ceramic bowl sinks dimensions 58/46 cm. Shell fastened to the wall with two screws with anchors and plas-constituencies inserts between screws and shellfish. Set the bowl on the wall at a height of 0.8 m from the floor. 2. Trap for wash basin with a rosette and chain JUS M.C5.810 chrome with the outer surface 3. Standing single lever mixer with spout with movable pipe and aerator. The set built is paid per piece built-in sinks. | 58 x46 cm | 6,00 |  |
| 3.Supply and installation of completele electrical boiler capacity of 50 lit / 2000 W, with complete accessories, thermostatic safety valve and the nickel tubes for the connection. Payoff per piece. | 50 lit/ 2000 W | 1 × |  |
|  | 10 lit/ 2000 W | 1 × |  |
| 4.Supply and installation of completely acrylic shower trays with: 1. Outflows from the tub 2. Above shower trays on the wall at a height of 0.9 m from the floor set up a wall mounted single lever battery for bath with wall rail and hand shower 3. At the appropriate place on the wall above the tub set up a chrome grip for tub length of 300 mm. The completely built bath is being paid for per piece of mounting shower trays depending on the size of the tub. | Angular shower - bathtub dim 80/80 cm | 1,00 |  |
| 5.Procure and install a one-piece sink cabinet made of sheet steel consisting of the following elements: 1.One-piece sink cabinet with upper part stainless steel. 2.Drain for water over nickel outflows connected with overflow, with chain, stopper and siphon - fat collector with a possibility of using the drain from dishwasher. 3.Standing single lever mixer with spout with movable pipe and aerator and the compound with low constructional water heater. All completely assembled and tested, with additional material to be paid per piece. | * one peace 80 cm | 1,00 |  |
| 6.Supply and installation of a set of mirrors measuring 50 x 35 cm, with galvanized storey. Calculation per piece of built-in mirror. | pcs | 6,00 |  |
| 7.Supply and installation of chrome soap dispenser at the sink, chosen by the designer. Payoff per piece. | pcs | 6,00 |  |
| 8.Supply and installation of nickel double movable towel holder - rod. Fitting next to the sinks. Payoff per piece. | pcs | 6,00 |  |
| 9.Supply and installation of two nickel-plated holders with glass cups. Payoff per piece. | pcs | 6,00 |  |
| 10.Supply and installation of galvanized hooks for towels - mesh. Payoff per piece. | pcs | 1,00 |  |
| 11.Supply and installation of toilet paper roll holder with lid. Holder is to mounted on the wall next to the toilet seat according to the manufacturer's instructions. Payoff per piece. | pcs | 6,00 |  |
| 21.ELECTRIC ASSEMBLING WORK: |  |  |  |
| 1.Relocation of existing measuring and distribution cabinet MRO with measurement groum; upgrading of 9 units. automatic fuses "C" 32A; ordinal clamps, entries and other unspecified material. | pcs | 1,00 |  |
| - 1 piece.GS switch 40A; 1 piece.FID switch 25/0,03A ; 1 pc. stair machine; 5 pcs. automatic fuses 10A; 1 pc. automatic fuses 6A; 20 pcs. automatic fuses 16A; ordinal clamps, entries and other unspecified material. | pcs | 1,00 |  |
| 3. Delivery and assembly of distribution board RT-1 made of twice pickled sheet metal or plastic material in color at the request of investor, adapted for installation in the wall, in which the following equipment was built: 1 pc. FID switch 25 / 0,03; 1 pc. GS switch 40A; 5 pcs. automatic fuses 10A; 1 pc. automatic fuses 6A; 20 pcs. automatic fuses 16A; ordinal clamps, entries and other unspecified material. | pcs | 1,00 |  |
| 22. UTILITY LINES: |  |  |  |
| 1.Delivery of material and production of the supply line, respectively (replacing the existing one ) cable type N2XH-J 5x25mm2 laid into the wall below the mortar, from the old position of the MRO to the new position of the MRO. All material is to be paid for and the labor per meter in total length. NOTE: The exact length is to be measured on the spot in the presence of the supervisory authority. | m | 20,00 |  |
| 2.Delivery of material and production of the supply line for the lift , cable type N2XH-J 5x10mm2 from the MRO to DB of the lift wage All material is to be paid for and the labor per meter in total length. NOTE: The exact length is to be measured on the spot in the presence of the supervisory authority. | m | 10,00 |  |
| 3.Delivery of material and production of the supply line , cable type N2XH-J 5x10mm2 in the wall under the mortar, from the the MRO to DB1 and DB2. All material is to be paid for and the labor per meter in total length. NOTE: The exact length is to be measured on the spot in the presence of the supervisory authority. | m | 18,00 |  |
| 23.INSTALLATION OF LIGHTING AND CONNECTORS: |  |  |  |
| 1.Material delivery and installation of the lamp conductor N2XH-J 2,3,4x1.5mm2 in the wall under the mortar,kit with the installation of junction boxes, veko clamps and single line, serial or alternating switches (switch) 10A 250V for the wall SRPS N.E3.130. In position is included the oulets for fans. The average length of bulb place is 8m. | pcs | 64,00 |  |
| 2.Material delivery and installation of the stair bulb place, conductor N2XH-J 4x1.5mm2, in the wall under the mortar, kit with the installation of junction boxes, veko clamps and push button switches 10A 250V for the wall. The average length of bulb place is 12m. | pcs | 6,00 |  |
| 3.Material delivery and installation of monophasic connection post conductor type N2XH-J 3x2.5mm2 in the wall under the mortar with the production of grooves, installing junction boxes veko clamps and sockets 10 / 16A 250V SRPS.N.E3.501 / 532 duopolistic for the wall with earthing contact and porcelain inlay. The average length of the connection point 10m. | pcs | 35,00 |  |
| 4.Material delivery and installation of three-phase connection place with conductor N2XH-J 5x2.5mm2 in the wall under the plaster kit with the production of grooves, with the installation of a connector 16A 380V SRS.N.EO.350 and mounting box 70mm type C SRPS.N.E1.122 with an earthing contact and zero contact (tripolar with porcelain inlay). The average length of the connection point 10m. | pcs | 1,00 |  |
| 5.Delivery of material and production installation of excerpts for connection of the boiler in the bathroom cable type N2XH-J 3x2,5mm in the wall under the mortar set with the production of grooves. The average length of the connection point of 8m. | pcs | 1,00 |  |
| 6.Delivery of material and production installation of excerpts for connection of heaters in the bathroom cable type N2XH-J-3x2,5mm in the wall under the mortar, kit with the production of grooves and connectivity. The average length the connection point of 8m. | pcs | 1,00 |  |
| 7.Delivery and installation of the indicator (switches) for the bathroom wall in a plastic box with indicators and switches: light, boiler and heater Set in front of the bathroom door at 1.6m from the floor. Completely produced. | pcs | 1,00 |  |
| 8.Delivery of material and production installation of excerpts for connection of the boiler in the kitchen with the installation of a kip switch cable type N2XH-J 3x2,5mm in the wall under the plaster kit with the production of grooves. The average lenght of the connection place is 11m. | pcs | 1,00 |  |
| 9.Delivery of material and production installation of excerpts for connection of the pump pool cable type N2XH-J 3x2,5mm in the wall under the mortar, complete with the production of grooves. The average length of the connection point 17m. | pcs | 2,00 |  |
| 10.Testing of the installations and issuing expert findings by an authorized organization. | Lump sum | 1,00 |  |
| 24.INSTALLATION OF SAFETY-PANIC LIGHTING: |  |  |  |
| 1.Material delivery and production installation of the connection point for the connection of panic lights, conductor type N2XH-J 3x1.5mm2, in the wall below the mortar with the installation of junction boxes veko clamps. The average length of the connection point 15m. | pcs | 9 |  |
| 2.Delivery and installation of security PANIC lamps on the wall or ceiling with NiCd battery powered of the following voltage 220V / 50Hz, with the marked arrow on the direction of the exit or sign EXIT according to the drawings, and a fluorescent lamp 8W and automatic circuit for charging the battery. The degree of autonomy of the product is 3 hours | pcs | 9 |  |
| 25. LIGHTS AND BULBS: |  |  |  |
| 1.Supply and installation of surface-mounted fluorescent lamps 2x36W with "V" grid (protection IP 20) type for example. 2x36W by the choice of investors. Complete with fluorescent tubes of 36W type Lumilux 840 and electronic ballast | pcs | 52 |  |
| 2.Supply and installation of lamps for the ceiling in the staircase area with white opal glass 250mm with porcelain E27 socket SRPS N.L5.110 b and the bulb 60W 230V in order to protect IP-43rd | pcs | 12 |  |
| 26.LIGHTNING ROD INSTALLATION: |  |  |  |
| 1.Delivery of material and strip grounding Fe/Zn tape 25x4 mm type P 25 SRPS N.B4.901C0000. Tape is laid by the objects for connection of the tubular earthing rods. | m | 15 |  |
| 2.Delivery of material and measuring circuit. Measuring compound derived with delimiters type D 'tape-tape'' SRPS N.B4.932 in a box for surface measurement circuit in the shape of A SRS N.B4.912 at the height of 1.5-1.7 m above the sidewalk. | pcs | 2 |  |
| 3.Material delivery and connection to the earthing tape, for exhaust lines and SIP Interconnection with Fe / Zn strip type P 25 SRPS N.B4.901 C0000 by crossed pieces 90x90 mm SRS N.B4.936 / II, the average length of 4m. Crossing part pour with bitumen in K.U.K. 90x90mm. | pcs | 3 |  |
| 4.Material delivery and installation of equipment for the early start time precedence with 25 micro seconds | pcs | 1 |  |
| 5.Delivery of material and laying tape Fe / Zn 20x3mm type P 20 SRPS N.B4.901 COOO in the wall under the facade for reception line and the roof at the appropriate carriers | m | 25 |  |
| 6.Delivery and installation of crosspoint pieces SRPS N.B4.936 dimensions 58x58mm for strapping in places of branching-crossing strips. | pcs | 10 |  |
| 7.Delivery and installation of galvanized steel pipes 6/4 " 4m in length, and fixing on the roof and tensioning the steel cables. | pcs | 1 |  |
| 8.Delivery and installation of cable P / Y 1x16 mm for connecting rack cabinet, TV cabinet and other metal masses | m | 30 |  |
| 9.Production of a tubular earthing rod using galvanized steel probe 3m 2 ". 2 probes are envisioed per down line | pcs | 4 |  |
| 10.Testing of lightning protection installation, measurement of transient resistance and issuing attest. | Lump sum | 1 |  |
| 27. INSTALLATION OF SCS (telephone-computer network): |  |  |  |
| 1.19" Rack cabinet, characteristics: - dimensions of 600x600, 16U, height 810 mm - reversible front door made of the protective glass with integrated lock and key - equipped with 2x19 "vertical carriers - cable entry at top and bottom of the cabinet - perforations on the upper side for natural ventilation or fan addition - maximum load of 48kg - equipped with a grounding kit - color RAL 7035 Legrand | pcs | 1 |  |
| 2.19 "patch panel equipped with with 24 x RJ45 connector, Cat. 6 UTP Characteristics: - automatic grounding of each connector - equipped with a 4 patch units, wherein each contains 6 LCS2 RJ45 connectors In accordance with the following standards ISO/IEC 11801 ed. 2.0-2, EN 50173/2 and TIA/EIA 568C Legrand | pcs | 1 |  |
| 3.LCS2 19 "Voice (telephone) patch panel (digital - contacts 3-6 / 4-5), contains 4 x 12 RJ45 connectors, 1U size, color anthracite, Legrand. | pcs | 1 |  |
| 4.19 "panel for horizontal cable management 1U, Legrand | pcs | 2 |  |
| 5.19 "panel equipped with power outlets, 8x2P + E and 1x switch, panel size of 1U, Linkeo, Legrand | pcs | 1 |  |
| 6.Fixed shelf depth of 360mm height of 2U, maximum load - 15 kg, to be mounted on 2x19" vertical carriers, for cabinets of 600mm depth, Linkeo, Legrand | pcs | 1 |  |
| 7.Delivery and installation of the rack cabinet - telephone switchboard | pcs | 1 |  |
| 8.Delivery and installation of phone system at the reception | pcs | 1 |  |
| 9.Delivery and laying of the PVC pipe Ø 16 mm in the wall under the mortar as preparation for the distribution of UTP cable from the concentration distributation (rack cabinet) to the user RJ45 sockets | m | 300 |  |
| 10.Material delivery and production of the installation from the rack cabinet in the already laid pipes in the wall below the mortar, conductor UTP Cat6 4x2x0.6mm with the installation of the junction box to the wall with mounting sockets and RJ45 connector, the average length of 20m. | pcs | 36 |  |
| 11.Delivery and installation of of the telephone cable JEhSTh 5x2x06mm from the existing telephone connection pole to Rack cabinet | m | 20 |  |
| 12.Delivery and installation of sockets for the wall and double-socket RJ45 CAT6 UTP, Legrand product or similar | pcs | 18 |  |
| 13.Testing of the network installation, issuing expert findings | Lump sum | 1 |  |
| 28. EQUIPMENT AND MEANS FOR FIRE PROTECTION: |  |  |  |
| 1.Handheld fire extinguishers, type S-9 A for extinguishing the initial fire, Supply, delivery and assembly. | pcs | 7,00 |  |
| 2.Metal plate of the following dimensions 400x300 mm with an inscription: “ INSTRUCTIONS FOR USINGTHE FIRE EXTINGUISHER ”and with the described procedure of use. Supply, delivery and assemblywith prefabricated material. | pcs | 7,00 |  |
| 3.Metal plate of the following dimensions 400x300 mm with an inscription: “ PROCEDURES IN CASE OF FIRE ”and with described procedure of behavior in the case of fire. Supply, delivery and assembly with prefabricated material. | pcs | 3,00 |  |
| 4.Metal plate of the following dimensions 300x200 mm. with a fluorescent inscription: “ NO SMOKING” Supply, delivery and assembly with prefabricated material. | pcs | 14,00 |  |
| 5.Metal plate of the following dimensions 400x300 mm with an inscription: „RESTRICTED ACCESS TO THE UNAUTHORIZED PERSONNEL ”Supply, delivery and assembly with prefabricated material. | pcs | 1,00 |  |
| 29.STABLE SYSTEM PROJECT FOR AUTOMATIC FIRE DETECTION: |  |  |  |
| 1.Supply and installation of fire alarm control panel, with back-up power 7Ah, and with all related modules i and putting into proper operation. SRPS EN 60896-21:2010, -SRPS EN 60896-22:2010, attested SRPS EN 54-2:2008, All material is to be paid for along with the labor | pcs | 1 |  |
| 2. Analogue addressable heat detector similar to the type of ATG at the base of YBO-BS: Individual adjustment of the sensitivity threshold in % / m, auto-compensantion of dirtiness, "flat response" technology, almost equal sensitivity to all kinds of puffs, attested SRPS EN 54-7:2008 | pcs | 1 |  |
| 3.Delivery and installation of analog-addressable optical smoke detector similar to the type of ALG-E at the base of YBO-BS: Individual adjustment of the sensitivity threshold in % / m, auto-compensantion of dirtiness, "flat response" technology, almost equal sensitivity to all kinds of fumes, attested SRPS EN 54-7 | pcs | 15 |  |
| 4.Delivery and installation of manual fire detectors HCP-E (MCP-E) for indoor installation with housing for wall mounting, attested SRPS EN 54-11:2008. All material is to be paid for along with the labor. | pcs | 5 |  |
| 5.Delivery and installation of cable JE-H (St) H FE180 / E30 2x2x0,8mm to connect the sirens.The cable is laid on the wall and on the ceiling on the E30 clamps. Testing according to DIN VDE 0472 part 804 and IEC 60332-3 method C), All material is to be paid for along with the labor. | m | 15 |  |
| 6.Delivery and assembly of electro dynamic alarm siren QAS-2, 24 V, 112 dB / 1m. SRPS EN 54-14:2008. All material is to be paid for along with the labor. | pcs | 2 |  |
| 7.Delivery and laying of cable type halogen-free JH (ST) H-0 2x2x0,8mm to connect detectors with a central fire alarm system. The cable is laid in the flexible hoses ⌀ 13mm in the ceiling and on the wall below the mortar. The average length of the detector place is around 15m. The price includes the purchase and installation of hose and cable. SRPS EN 60332-3-24:2010.All material is to be paid for along with the labor. | pcs | 21 |  |
| 8.Delivery and laying of cable type N2XH-J 3x1.5 mm to power the fire panel from the nearest junction board. Fuse 6A is going to be installed in the junction board. The cable is laid in the wall below the mortar. All Material is to be paid for along with the work per meter length | m | 10 |  |
| 9.Installation, connection, with any additional required and not specified small elements of the system, adjustment, commissioning and user training for the use of the installed equipment. Submission of attest documentation. | Lump sum | 1 |  |