# VOLUME 3

# TECHNICAL SPECIFICATIONS

###### TECHNICAL SPECIFICATIONS

These conditions are the basis for the execution of works, in accordance with Serbian legislation, if not specified otherwise in General and Special conditions for Works Contracts (Volume 2, Section 2 and 3).

SECTION 1: GENERAL  INFORMATION

## 1. Scope and description of the construction works

The reconstruction should be done in the following works/equipments:

- STABLE AUTOMATIC INSTALLATION FOR WATER BASED FIRE EXTINGUISHING “SPRINKLER INSTALLATION”,

- SMOKE AND HEAT EXHAUST VENTILATION SYSTEM,

- HEATING, VENTILATION AND AIR CONDITIONING SYSTEM,

- ELECTRICAL WORKS FOR THE ELECTRICAL INSTALLATION OF STAGE LIGHTING.

The implementation of the contract shall be executed with full compliance with the description of the main project which is an integral part of tender documentation. The main project includes explanatory notes, bill of quantities and design drawings.

2. Work schedule

The work schedule shall be specified in the Implementation Programme to be prepared by the Contractor and to be approved by the Contracting Authority.

# SECTION 2: GENERAL REQUIREMENTS

1.	STANDARDS

As a minimum the Serbian standards and codes shall always be satisfied where applicable. Other internationally acknowledged standards and codes may be used only if:

- They are more or at least equally stringent compared to the respective Serbian standards and codes or

- no applicable Serbian standards and codes exist for the specific case.

The materials which are used must correspond to the requirements of the standardized documents asset in Republic of Serbia.

If the Contractor should wish to supply material or execute work to an alternative national standard or international specification he shall give full details of his proposal in writing to the Supervisor.

2.	CONTROL OF WORKS

2.1	Contractor's equipment

The Contractor shall furnish equipment which will be efficient and appropriate to secure a satisfactory quality of work and a rate of progress which will insure the completion of the Works within the time stipulated in the Tender. If at any time such equipment appears to be inefficient, inappropriate or insufficient for securing the quality of work required or for the rate of progress, the Supervisor may be entitled to order the Contractor to increase the efficiency, change the character or hire additional equipment, and the Contractor shall conform to such order.

2.2 	Protection of existing structures and utilities

The Contractor shall assume full responsibility for the protection of all buildings, structures and roads existing in the area of the construction site, public or private, whether or not they are shown on the drawings.

The Contractor has to pay special attention to avoid any damages on any protected areas.

Any damage resulting from the Contractor's operations shall be repaired at his expense.

2.3	Safety and security on site

Safety and security arrangement should be performed in accordance with article Serbian Law on planning and construction and related regulations.

2.4	Handling and storage of materials and plants

All materials and plants to be incorporated in the work shall be handled and stored in a manner, which prevents injury of any kind whatsoever. Any materials or plants which, in the opinion of the Supervisor, have become too damaged to be fit for the use intended or specified shall be promptly removed from the site, and the Contractor shall receive no compensation for the damaged material or its removal.

2.5 	No specific provision

Where no specific provision is made in the Bill of Quantities for work of a temporary nature, it shall be considered as covered by the Lump sum prices entered in the Bill of Quantities.

2.6	Approval of sources, materials and plants

Materials and plants incorporated must originate in a Member State of the European Union or a country covered by the Bulgaria-Serbia IPA Cross-border programme. Material that originates from sources, which are not approved by the Supervisor, cannot be used for Works.

Approval of a source does not mean that all material in the source is approved. The Contractor has to ascertain by continuous control check measurements that only material which complies with the requirements specified in the various clauses of these specifications will be used for the Works.

2.7 	Clean-up work

The Contractor shall clear way and remove from the site any wreckage, rubbish and temporary works, which are no longer required.

2.8	Responsibility of the Contractor

Approvals from the Supervisor do not relieve the Contractor from his obligations or responsibilities under the Contract.

3.	ADMINISTRATIVE SPECIFICATIONS

3.1 Implementation Programme

Implementation programme for delivery of works shall be prepared consistent with the duration of the project’s implementation and the works activities implementation. The programme shall be presented in a format which includes a bar chart of all the major activities. No later than five working days after the end of each month, the Contractor shall submit an updated programme to the Supervisor. This shall show, as a minimum:

- progress made during the past month, compared with planned progress

- activities planned for the next month.

3.2 	Progress meetings

The Contractor shall agree with the Supervisor and the Contracting Authority for dates for regular progress meetings. These meetings shall normally be held monthly, no later than 10 working days after the completion of each month.

3.3 	Quality assurance

The Contractor shall institute a quality assurance system to demonstrate compliance with the requirements of this contract. The system shall be in accordance with the details stated in the Contract. The Supervisor shall be entitled to audit any aspects of the system.

4.		IMPLEMENTATION OF THE WORKS

4.1	Materials

The Contractor shall use only materials that conform to the technical requirements set forth in the clauses of this Technical Specification (detailed description of codes in standards should be read from Main project).

All Materials and Plant supplied to perform the Permanent Works under the contract shall be new products. Second-hand Materials and Plant will not be accepted.

The Tender drawings constitute the drawings issued for construction/ installation/ execution.

4.2	Testing

Reliable shall be only the type and amount of tests performed in conformity with the prescription of this Technical specification, except when this right is granted to the Contracting Authority.

The Contracting Authority may require additional tests when the results obtained are uncertain.

Beside the tests specified in this Specification, the Contracting Authority may require additional tests to establish possible hidden omissions and effects. Costs for these tests shall be entirely at the Contractor’s expense if such defects are confirmed.

4.3	Inspection and measurement of works

The Contracting Authority may at any time inspect the quality and measure the amount of works performed. If this cannot be done with the Contractor’s assistance, a deadline shall be fixed for hiring external specialists. In this case, the expenses shall be paid by the Contractor.

5.	PREPARATORY WORKS

Before starting the works the Contractor has to perform some preparatory works at the site.

5.1	Boards and signs

The Contractor shall allow for installation and maintain in good condition a board with the name of the project and the co-financing institutions written in a way /text and font size/ conforming to the requirements of the Contract and in compliance with EU visibility guidelines and the guidelines by the Bulgaria-Serbia IPA Cross-border programme.

5.2 	Setting out the site

The Contractor shall in co-operation with the Contracting Authority set out the total site to be used for construction.

5.3 	Temporary facilities

The Contractor shall effects all expenditure for establishing, operation and removal of temporary facilities if such are needed for the good performance of the Contract. All needs for establishing such facility shall be duly justified.

5.4 	General supply facilities

###### Sanitary Arrangements

The Contractor shall provide for and maintain temporary sanitary facilities on the site for the use of all persons connected with the Works. The Contractor shall keep the facilities in a clean and sanitary condition, and shall post notices and take such precautions as may be necessary to keep the site clean.

###### Water supply

The Contractor shall provide for and maintain an adequate supply of potable water for his use. The water supply shall be used for construction purposes and for consumption in the temporary facilities.

###### Power supply

All electrical power required by the Contractor shall be provided by him at his own expense. The Contractor prior to taking-over of the Works shall remove all temporary installations if it is not agreed upon that the Contracting Authority takes over the installations.

# SECTION 3: GENERAL TEHNICAL CONDITIONS FOR EXECUTION OF ALL WORKS

All provisions of these technical requirements are integral part of each item of Bill of Quantity with the following text:

All works to be done according to description of certain items, introductory descriptions for certain groups and types of works, details, technical description, static of calculation and other attachments and drawings of this Design.

Lump sum price of each item of the bill of Quantity includes all necessary elements for its calculation per a quantities so that they can be clearly and finally stated in the pro forma invoice such as:

MATERIAL

Value of the material is the purchasing price of the main, auxilliary connecting material and similar together with calculation of transport costs regardless to type of vehicles, with all handling, loading, unloading, storage and keeping at the construction site against damage, relocation, protection, and similar as well as taking sample for testing.

COSTS OF WORKS

Price should include the value of main and ancillary labor for required operations, all work in indoor horizontal and vertical carriage and all required work for protection of finished works and constructions against harmfull effects, other works, overheat, cold, rain, etc)

All costs for machinery.

ANCILLARY STRUCTURES

All kinds of scaffolding regardless the height and similar are included in the lump sum price of the work they are required. Scaffolding must be placed in time, not to disturb normal operation and the price includes: disassembly, manufacture and installation, amortization, disassembly and moving from the construction site.

The price includes all obligatory fences, protection of trees and greenery, protective covers, accesses, spreading when eartworks are concerned, bridges for manipulation in excavations of higher depths.

Depriciation is calcualted only for the anticipated time of use.

All necessary shuttering, regardless the type is included in price of the work it is needed and is not charged separately.

Shuttering includes all necessary supporting and: production, placement, disassembly, cleaning and arranging after removal. The shuttering price includes also its wetting and preparation for concreting.

Upon the completion of concreting, all shuttering is to be removed after certain defined time, clean and sort, that is prepare for the next use and taken away from the site upon the completion of works.

OTHER COSTS AND LEVIES (FACTORS)

Value of works needed for renumeration of personal income for certain item shall be calculated with a partticular Contractor's factor which is formed based on the existing regulations and instruments as well as own particular business of the Contractor, all costs for payment of contributions (taxes, fees, interest, insurance, earnings, funds, fixed assets, business costs, etc).

In addition to this, Contractor shall use factor for the following works which shall not be paid separately as additional work or pre-invoice item:

- all hygienic-technical protective measures for personal hygiene of workers and protection of the structure and surrounding such as: fense, bridges, covers, various ancillary and sanitary premises, etc:

- all horizontal and vertical marking and labeling prior to commencment of excavation work and later when the building is constructed;

- cleaning and keeping tide during construction, removal of waste, litters, except final cleaning and washing prior to commissioning that shall be calculated and paid as a separate item;

- control of the structure shrugging and monitoring;

- all necessary testings of materials and procurement of required attestation and certificates, especially for concrete, cement, brick, lime, sand, etc:

- development of the construction site and land, newly constructed structures used for the construction site, that is its development without any construction material, dirt, waste, traces of digging, etc and demolition of all ancillary facilities.;

- ensuring space for storage of material and tools, sub-contractors, craftsmen and installation workers-this is provided by the Investor;

- possible protection of the structure (conservation) in extreme periods. In case the construction of the facility is done during summer period, the Contractor shall be obligated to protect the facility against ruin and freezing and all damaged parts caused by ice and frost or something else to repair when continuing works and bring into function on its own expense. This protection need to be provided in summer period from too fast drying at similar with care of the structure after, for example, wetting of the concrete;

- Contractor shall not charge subsequently the Investor with increased costs in case it perform works in winter period for costs of possible heating of the facility or increased per diems for work during frost since it is considered to be the problem for the Contractor and its organization for performance of work if not otherwise contracted.

- Insurance of the facility during work performance with the Insurance company is also the obligation of the Contractor, and it is understood that it is included in calculation as a factor.

- none special costs either stated or not in this text shall not be separately acknowledged and approved in lump sum prices for each work. According to these conditions, description of certain specific items for every work. According to these terms and conditions, description of certain items-certain work, a lump sum price should be composed for each item in the pre-invoice.

All these provisions are valid for craftsman and installation works provided that the Contractor must anticipate remuneration of all overhead costs related to assistance and engagement of labor, material, tools and other if such work is done through sub-contractor. All these relationship must be precisely agreed so that Investor cannot be charged with any additional costs. Especially, pay attention to synchronization of works since no costs after made installations in the walls, over walls and other structures shall not be approved or acknowledged.

MEASURES AND CALCULATION

In every item of calculation, the manner for calculation is stated.

In case certain items lack the manner for calculation of works, apply and abide fully to valid applicable norms and standards in civil engineering.

OTHER

In case the Contractor find some archeological remnants during performance of earthworks, it shall be obliged to apply regulations on keeping such findings and to immediately inform the Supervisory body and competent institutions.

In case during performance of earthworks, the Contractor discover any known or unknown installations, they must be protected from damage and immediately inform the supervisory body and competent institutions for the purpose of making decisions on their removal or relocation and these costs shall be borne by the Investor.

On the site where a new building is constructed, if there are some structures, facilities which need to be demolished, demolition or destruction of such facilities shall be performed by the Investor in its arrangement and no demolition shall be included in this pre-invoice calculation.

All required material must be of good quality and fully correspond to conditions and provisions of SRPS standard.

All works must be performed according to valid technical regulations, with due care and good quality.

All other works and obligations which have not been mentioned shall be regulated in spirit of the Law on construction of facilities and other regulations which regulate this issue, valid standards and average norms in civil engineering.

According to these conditions, description of each item and descriptions of group of works, lump sum price should be composed in the pre-invoice estimation.

This shall be valid for craftsman and installation works as well, provided that the Contractor of main work must anticipate remuneration of all overhead costs related to assistance and engagement of labor, material, etc related to additional works whether they shall be carried out by Contractor or sub-contractors. In case the Contractor agrees and accepts the works related to built-in of equipment  (equipment installation) and organization, it must anticipate it through the contract with Investor.

# SECTION 4: GENERAL DESCRIPTION FOR SPECIFIC WORKS

4.1.	STABLE AUTOMATIC INSTALLATION FOR WATER BASED FIRE EXTINGUISHING “SPRINKLER INSTALLATION”

For the purposes of the facility, the stable automatic installation for sprinkling water spray fire extinguishing – the sprinkler installation, has to be developed.

Entire facility consists of the underground and aboveground parts. In the underground part, there are stores and a sprinkler station, whereas the aboveground part consists of offices, a stage, an auditorium with balcony, dressing rooms, halls…

The automatic sprinkler system distribution has to be based on this division.

Regarding distribution, wet pipe sprinkle system has been envisaged according to the investor’s request. Bearing in mind that the facility is heated throughout the year, temperature will never drop below 5°C. The wet sprinkler installation will be an automatic fire protection system.

For the Cultural Centre facility reconstruction, the sprinkler installation for sprinkling water fire extinguishing will be installed on the GF+I level. In the basement, level -2.86, the sprinkler station will include sprinkler installation vents. Water will be supplied under conditions set out by PE VODOVOD in Surdulica.

- In the basement, level -2.86, sprinkler station will be located with a fire resistance of 2h to other rooms

- Wet pipe sprinkler installation in the basement for the auditorium, balcony, stage, backdrop, side stage

- The I floor for dressing rooms and rehearsal rooms,

- The II floor for dressing rooms and halls

Other premises, technical rooms, archives, and offices will be extinguished by mobile equipment/hydrants and fire extinguishers. All rooms has to be covered with fire alarm systems through which all extinguishing systems for the facility has to be performed, with a complete alarm system and a system for evacuation of visitors.

According to the Regulation EN12845 Sprinkler protection scope, sanitary blocks and hallway do not have to be protected.

Theatres (facilities with a separate stage)

Theatres with a separate stage (with a safety curtain between a stage and auditorium), has to be provided with a line of drenchers controlled by a quick opening valve (e.g. a plug valve) fitted in an accessible position. The water supply for the drenchers should be in front of the alarm sprinkler station. A stage will be protected by the drencher installation with automatic and manual activation. Stages at a total height of maximum 12 m can be alternatively protected by the sprinkler installation.

All workshops, dressing rooms, storerooms as well as rooms under the stage should be protected by the sprinkler installation.

In compliance with Articles of EN12845 standards, one drencher protects maximum 12m2, under condition that all requirements for drencher distribution are met.

Necessary water quantities, complying with standards, amount to 5l/m2. Working time of the installation is 60 minutes, and maximum protected surface from one drencher is 12m2.

Drenchers shall be placed face down (hanging) set under the ceiling.

In the sprinkler station there is equipment in the function of automatic sprinkler installation. The main factors are safe supply of water and automatic installation activation in case of fire. Water with the connection from the town water supply network is used as a supply. In accordance with EN12845 standards where main pipelines start their way towards rings and drenchers, there is a single duct with non-return valves (in order to regulate water flow). This duct is used to be connected to the fire truck in case of emergency. On the façade there is a cabinet with the connection (quick couplings B type) which is used to directly connect a fire truck to the extinguishing system. Connection on the façade is selected in a way which enables easy access to a fire truck. The cabinet is placed on a wall with the coupling which is 1200mm far from ground level. In a safety box there is a connection, quick couplings B type, which are connected by a separate pipe DN 100 to the sprinkler station. The pipe has a non-return valve and a valve for proper water flow. On the pipeline, there is a drainage valve, too. In case of fire, a fire truck is connected to the sprinkler installation over the connection of the façade. Upon fire extinguishing, the pipeline connected to the sprinkler station will be full of water.

4.2.	SMOKE AND HEAT EXHAUST VENTILATION SYSTEM

The main objective of the smoke and heat exhaust ventilation system in case of fire, is to provide efficient smoke and heat exhaust ventilation of places that cach fire.

Installation of the smoke and heat exhaust ventilation system is defined on the basis of requirements from laws and regulations prescribing the obligation of the installation of this system in facilities with the increased risk of fire, difficult evacuation and difficult intervention of fire fighters.

According to the Technical recommendation for fire protection of residential, business and public buildings - SRPS TP 21, the CCS facility is classified as  IJ2 (separate public building from 8 to 15 m).

The facility includes a space for audience divided in auditorium and a balcony. This is a space for maximum 200 visitors.

For this space, forced smoke and heat exhaust ventilation is envisaged in case of fire according to the mentioned standard.

The smoke and heat exhaust ventilation system has to meet the following conditions in case of fire:

- fire-resistance of smoke exhaust ducts for at least 2h

- smoke exhaust ventilator has to work in case of fire and has to be constructed in a way to withstand temperature up to 400 ºC for 90 min

- apart from automatic control of the system, there has to be a possibility of manual control from a safe place.

- a ventilator is power supplied during fire. The ventilator cables have to be protected from the fire for two hours.

- There is a backup source of power supply (diesel generator)

Smoke exhaust is achieved by opening a smoke damper 1120 x 800, which is placed in a flue 1120 x 800 mm and a centrifugal roof ventilator to the outer atmosphere.

Loss of power opens a blade by a force of return spring, and with new position of electric actuator under voltage, the blade goes back to normal, closed position.  In the actuator there are contacts signalizing the blade position.

The smoke and heat exhaust ventilation system elements from the auditorium space has to meet the following criteria:

- roof ventilator, 400ºC, 120 min in compliance with SRPS EN 12101-3 standard, certificate of conformity (manufacturer’s declaration)

- a smoke damper: fire resistance of a smoke damper is 120 min in compliance with SRPS EN 12101-8, a trial according to SRPS U.J1.174, certificate of conformity (manufacturer’s declaration)

- smoke extraction ducts have to be examined according to the SRPS EN 1366-9 standard, report on examination.

4.3.	HEATING, VENTILATION AND AIR CONDITIONING

For the selection of heating, ventilation and air conditioning installation, type of activities and contents for an audience have been taken into account, considering that all main events for the audience last short, i.e. up to three or four hours, twice a week, which is a significant factor for the installation design. The auditorium is provided with microclimate conditions: internal temperature, relative humidity, amount of fresh air, noise level, and air flow velocity.

The air system of single duct ventilation and air conditioning has been envisaged, too. Air heats and cools space, where 100% of fresh air in the total amount of 4000 m3/h has been planned, which is selected on the basis of maximum number of visitors provided in the ToR.

Regarding approved air amount (in accordance with regulations) for such type of building, 20 m3/h of fresh air per person is necessary, that is, 4 air changes per hour.

Air chamber provides the following functions of air treatment:

- Intake of outside fresh air

- Fresh air filtering

- Air heating

- Air cooling

- Distribution of treated air to the auditorium and insertion of air in the auditorium space.

- Exhausting air from the auditorium space in the outer environment through overpressure dampers.

Air distribution is carried out by a rectangular duct made of galvanized steel sheet and a ceiling diffuser. Air flow velocity in a ventilation duct and ceiling diffusers are selected so that they cannot cause a noise level outside values allowed by rules.

4.4.	ELECTRICAL WORKS FOR THE ELECTRICAL INSTALLATION OF STAGE LIGHTING.

4.4.1. 	Power supply in the facility

Power of the Main Distribution Cabinet (MDC) for the stage lighting in the SCC will be supplied from the MDC of the facility by placing an electro energetic cable N2XK 5X25mm2, on the Perforated Cable Tray (PCT). Cable cuts are provided in the single-pole schemas in the graphic section.

4.4.2.		The Main Distribution Cabinet

The Main Distribution Cabinet (MDC for the stage lighting) is made of the insulating material -polyester. MDC for the stage lighting is installed on the ground floor, the room no.13 at the height of 1.6m from the floor to the lower edge of the cabinet.

The MDC is equipped with necessary equipment for reflector power supply, consisting of corresponding switches, Residual Current Devices (RCD) and fuses according to the single-pole schema. The lighting installation will be carried out by the N2XK cables with an adequate number of conductors and necessary cut. The conductors will be laid in the cabinets on the wall.

All consumers with boxes made of electrically conductive material, will be earthed over the third and fifth conductor together with all sockets.

4.4.3. 	Electrical lighting- lighting installation

Electrical circuits of the lighting will be supplied by N2XK 3.4 and 5x1.5mm2 conductors. The conductors will be laid in the cabinets on the wall.

Installation switches will be placed at the height of 1.5m. The type of switch will be selected in compliance with necessary features: 250V, 16A.

For this facility, panic light 8W is envisaged- with its own power source of autonomous operation of 3 hours,  8W - 3h type.

4.4.4. 	Other consumers

The project envisages an appropriate number of single-phase and three-phase power sockets with protective contact, for thermal consumers power supply. Connectors are installed on the wall according to the standards for certain premises, and in compliance with the single-pole schema with N2XK  3x2,5mm2 conductors.

4.4.5. 	Protection against electric shocks

Protection against electric shocks is regulated by TN-C-S system for the entire object, that is, differentiation circuit protection device, Residual Circuit Device (RCD) 63/05A.

4.4.6. 	Grounding

Additional grounding is envisaged for the facility, if the existing grounding is not satisfactory, as an earthing device, which will be carried out by galvanized steel band FeZn 25x4mm, placed in a trench 1.5 m from the building, with a necessary number of thermals from an additional trench for down conductors, vertical pipes etc. according to single-pole schema, and connected with the existing grounding over potential equalization bar.

Potential equalization bar will be connected with all metal masses of the facility that do not belong to any of the circuits. This bar is connected to the main grounding bar, with the separate conductor, placed immediately below the MDC, which connects all earthings (water supply, sewage, mental mass etc.).

4.4.7. 	Potential equalization

Potential equalization of the stage lighting equipment will be performed by the P/F-y 1x6 mm2 conductor, by connecting all metal masses permanently and efficiently and earthing them with an appropriate potential equalization bar, which is directly connected to the main grounding bar.

4.4.8.	Меаsurements and testing

Upon works completion and trial operation, measurements and tests will be carried out, in particular:

Check of galvanic continuity of the conductor

Check of differential protection for all circuits i.e. protection efficiency for each circuit individually.

Measuring insulation resistance on the energetic conductors and issuing expert findings about the quality of the measured values.

4.4.9. 	Automatic fire protection curtain

Fire protection curtain is installed in the main hall of the Surdulica Cultural Centre,  fire resistant 90-120 min. It is made of fibre glass fabrics, especially tested for fire resistance - it holds fire up to 1100 ° C for 90-120 minutes.

Threaded plate is 70mm thick and made of galvanized steel. Vertical pipes are galvanized 110 mm wide.

Speed of curtain closure is 7m/min. Upon fire occurrence, the curtain is automatically closed, even with supply interruption, thus activating optic and sound alarm.

On the lower part of the curtain, there is an additional contact safety rubber.

Dimensions of a panel 300x250mm and it enables all door functions up to 4 hours after power outage. On the panel, there is the command UP-STOP-DOWN button integrated.

Power supply of the curtain is 220/230V/50 X3/20 A. Electrical connector 3 x 2,5mm.

The curtain dimensions are 11250mm x 4500mm.

The fire resistant curtain has to be delivered with appropriate certificates from the manufacturer.

SECTION 5: PARTICULAR TECHNICAL SPECIFICATION

5.1. STABLE AUTOMATIC INSTALLATION FOR WATER BASED FIRE EXTINGUISHING “SPRINKLER INSTALLATION”

### 5.1.1.TECHNICAL DESCRIPTION

### FIRE EXTINGUISHING SPRINKLER INSTALLATION

Sprinkler installations are stable installations, which are activated automatically on the occurrence of fire and can provide high efficiency and safety during extinguishing.

This type of installation is among the most efficient fire extinguishing installations.

Working principle of the installation is water spray fire extinguishing from the sprinkler heads. Installation in the preparatory position, i.e. before its activation has closed sprinkler heads which are opened by a vial breaking as a response to increased temperature, and thus automatic activation starts together with installation. Pipelines carrying the water to sprinkler heads are under constant pressure. Depending on a type of installation, the pressure may be caused by the extinguishing medium, i.e. water or compressed air.

One of the most important features of the system is a quick response to occurrence of fire. Depending on the fire size, the system will work with one or more sprinkler heads according to fire spreading.

In addition to extinguishing, the installation triggers a fire alarm during the activation, thus alerting people.

The signal is sound due to alarm bells that are activated by the water turbines and it starts when the main flow of water lifts a dry sprinkler valve that sends a small amount of water to the little turbine, sounding the bell.

There are several types of fire sprinkler system

Depending on the fact whether the temperature is higher than +5ºC or not, in the protected room during winter, sprinkler systems are divided into:

- wet,

- dry

- combined.

The wet pipe sprinkler installation system has the advantage of temporary water based fire extinguishing, because the entire system is filled with water and is under constant pressure. Therefore, it is necessary to prevent freezing in the protected room throughout an entire year, in case of low temperatures.

In places where it is impossible to provide this system, dry sprinkler installation is used.

Entire sprinkler installation is composed of:

- Sprinkler station with a pressure maintenance system,

- Alarm valve station

- Vertical ducts,

- Pipe network with sprinkler heads and

- System for management of devices and signalization

When it comes to dry plants, pipelines can be conditionally divided in two parts (wholes) or the pipeline in front of the dry alarm valve and the pipeline behind the dry alarm valve.

### WET SPRINKLER STATION

On the basis of guidelines for the design of the sprinkler systems EN12845, and according to the fire risk assessment, the area of the cultural centre (where the stage should be separated from auditorium), belongs to a group OH4.

According to this, and bearing in mind the fact that in this area temperature does not reach less than 5°C, the wet system was adopted with a possibility of 1000 sprinkler heads for one valve.

Wet alarm sprinkler station is composed of the following main parts

- Wet alarm sprinkler valve DN150

- Valve DN150

- Water drain valve

- Alarm bell armature

- Manometers  0 - 16 (2 pcs)

- Pressure switch

- Alarm bell

WET ALARM SPRINKLER valve separates a pipe network with sprinkler heads from a water source. At the moment of vial breaking of any head, a valve opens, which enables water flow towards a hydraulic alarm bell and sprinkler heads. The valve body consists of an upper and lower chamber. The chambers are divided by a clapper.

The clapper lies in closed position on the grooved seat ring. There is a pipe towards a hydraulic bell, so when the clapper is open, there will be a flow of water towards a turbine of a hydraulic bell and a pressure switch.

HYDRAULIC ALARM BELL gives a signal in case of fire, that is, at the moment of opening of sprinkler heads.

HYDROELECTRIC PRESSURE SWITCH is placed on a part of a pipeline which leads from an alarm valve to a hydraulic bell. During the period when water flows from the alarm valve to the hydraulic bell, the water pressure closes fire detection circuit, which ends with a connection in the control device.

MANOMETRES are connected to a pipeline network in front of and behind an alarm valve, which enables pressure control in front of and behind the alarm valve.

VALVE DN100 is set up in front of an alarm valve and is intended for closure of water supply with the aim of: changing sprinkler heads, upgrading or reconstruction, analysing pipeline network and repairing.

In the operating state, the plug has to be completely open and sealed.

WATER DRAIN VALVE is connected to the upper chamber of the alarm valve and is intended for the water drain from the pipeline network upon activation of installation and in case of certain repairs. In the operating state, the valve is closed.

CONTROL VALVE R1/2" is connected to the lower chamber of the alarm valve. By opening the valve, water is brought in a bell and the hydroelectric contact.   During that process, there is no opening of the alarm valve clapper. It is used to control the work of a bell and the hydroelectric contact.

WATTER SUPPLY METHOD

As it has been pointed out, the water is supplied from the town water supply network. The connection from the town water supply network comes to the wall of the sprinkler station and the water pipe is DN150.

As an additional safety measure, there will be the connection with a quick coupling type B for fire extinguishing hoses for water supply from the fire truck. The connection is located in the protected cabinet, placed outside the facility, easily accessible in emergency case.  The cabinet is placed on a wall with the coupling which is 1200mm far from ground level. In a safety box there is a connection, quick couplings which is connected by a separate pipe DN 100 to the sprinkler station. The pipe has a non-return valve and a valve for proper water flow. On the pipeline, there is a drainage valve, too. In case of fire, a fire truck is connected to the sprinkler installation over the connection of the façade. Upon fire extinguishing, the pipeline connected to the sprinkler station will be full of water. The purpose of the drainage valve is to drain the water away. The water is drained to a drainage pit through the drainage pipe, set up on the ground of the sprinkler station. The drainage pit and water drainage are not part of this project.

The water, coming from the town water supply system, may contain dirt particles, which will contaminate and clog sprinkler valve elements. In order to prevent it from occurring, right at the beginning, in the sprinkler station, a filter for removing impurities is set on a pipe connected to the water supply network. It has valves in front of and behind itself. Valves are safe in the open position. Their condition is controlled by the staff in charge of installation, in compliance with rules and methods prescribed for such installations by a responsible person. Two manometers are envisaged to control a strainer, one in front of and one behind the impurity strainer. On the pipeline, in front of the manometers, there are taps, which are closed so as to maintain manometers. When there is difference between pressure in front of the strainer and pressure behind it, the filer is dirty and should be cleaned. Then, frontal and behind valves are closed, whereas a valve of a bypass pipe opens so as to enable uninterrupted water supply during the cleaning process. Water supply form the town water supply system to the sprinkler station is not concerned by this project.

At the entrance of the water supply pipeline to the sprinkler station and in front of the wet sprinkler valve, a round valve DN150 is set up, with a micro switch showing whether the valve is open or closed.

For the entire facility, one wet sprinkler valve is envisaged, where all fire fighting regulations are complied with. Total number of sprinkler heads is 94. At the end of the sprinkler station, at the -1 level, one vertical would be provided for the power of the entire facility.

### SPRINKLER STATION

Sprinkler stations are located in the underground level -1. This room is protected from low temperatures and it represents a separate fire sector resistant to fire for 120min.

In the pump station, along the walls, a vet valve is located. From the connection of the town water supply network, a connecting pipe is brought to the sprinkler station, where the filter for removing impurities is set up, together with a circulating pipeline and valves on both sides. This water should be clean, because it has been purified, but practice shows that dirt may occur and lead to clogging of a sprinkler valve channel. Therefore, according to the EN12845 standards, this set is envisaged at the exit of the town network and before entrance to the sprinkler valve. Under this filter, there is a metal drain for water, which cleans and maintains the filter. Drains are connected to pipes, which drain water away from various drainage and drains to the drainage pit.

The sprinkler valve contains a wet alarm bell, which gives a signal for fire occurence in some part of the facility, upon the activation of the installation. It is a turbine-type bell, which means that it is run by water.

Having left the bell, water is drained to a container and then to the sewage. Therefore, wet bells are installed outside the sprinkler station, below which there is a container for water necessary to run bells. After that, the water is drained away.

Connections for a fire truck are set up on the outer wall in the cabinet, which is easily assessable to a fire department. The cabinet is fitted at the height of 1200mm from the zero point.

### PIPE NETWORK WITH SPRINKLER HEADS

Water-based fire extinguishing with the sprinkler heads is envisaged in the entire facility.

The main distribution in the facility is carried out with a 10‰ incline for regular diameter pipes to DN50 and a 5‰ incline for larger diameter pipes. Therefore, all branches are inclined towards the main pipe, and the pipe itself is inclined. On the horizontal pipes there is a drainage valve for water drainage. At the places where the height of pipeline is the lowest (“lowest points”), drainage valves are set up, which empty the installation upon fire, testing or other situations during which water remains in pipelines. Upon water drainage, the drainage valves are closed. In order to prevent misuse of these valves, it is necessary to take off small wheels after closure, so as to avoid unauthorized operation.

Network with sprinkler heads, separated from the main track, that is, branches, can have maximum 4-6 sprinkler heads. In this way, balanced flow through branches is achieved, and pressure drop is reduced.

Sprinkler heads are face down. The main pipes of the pipe network are made of black welded pipes. Pipes will be welded, and armature will be connected through flange or threaded connection.

When fire occurs, a vial of a sprinkler head breaks as a response to increased temperature, and thus the closing element on the head is released.

In the other part of the facility, there is water under pressure behind alarm valves. The balance of wet pipes is maintained by water pressure in the pipeline behind the ridge. The pressure is a bit higher that the town network pressure. Since the valve ridge opens towards the part with network and sprinkler heads, the pressure enables a clapper to be still when there is no fire.

In case of fire, (in both dry and wet systems) there is large pressure drop (air goes out abruptly when the head sprays for dry systems, whereas water suddenly drains away for wet systems). Large pressure drop on the valve ridge causes an imbalance of pressure in front of and behind the ridge. Water, in front of the ridge, which now has much greater pressure on the ridge (from air within dry and water within wet valves), opens the valve and enters a chamber. Then it goes to a hydraulic bell and signalizes fire. Water then goes to the fire place and it forms rain of drops over heads, which actually extinguishes fire. On its way through the flow indicator, it signalizes fire. Water prevention is only possible by manual intervention on the valves.

SPRINKLER HEAD is a basic element of the installation. It has dual role:

- water spray fire extinguishing in the form of a parabola uniformly filled with water drops

- fire alarm- imbalance after a vial breaking as a response to increased temperature is used as a fire indication.

Sprinkler head is composed of:

- Head frame,

- Valve with cap

- A vial which breaks when temperature reaches 68 Cº

- Sprayer at the top of head frame

Pipe network is branched under the ceiling of the protected premises. It consists of the main pipeline and pipe branches. At the ends and along branches there are twisted sprinkler heads. When it comes to a dry system, the heads are standing, face up. In the dry system, branches should be on the top of the main pipeline or on the side in order to ensure gravity discharge. However, wet system branches do not have to be on the top. Under no circumstances is it allowed to form branches below the pipeline, regardless of the system type.

“Fast Response“ heads are envisaged in the entire facility due to the request of the investor, importance of the building and out of safety reasons. The main pipes have branches with sprinkler heads.

Branches and the main pipe are welded.

Pipes and diameters profiles ≤50 mm must not be welded on the site. Flame cutting, soldering and other types of thermal processing, carried out on the spot, are also not allowed on the site.

Welding on sprinkler installation pipes are carried out so that:

- All connections are fully welded

- Inner side of welded seams cannot obstruct water flow

- Connections and welded remains are removed from the pipeline

Welders must be attested in accordance with the EN 287-1.

Welding is not allowed for pipes or connections with diameters less than 50mm, except in cases when welding and control were not performed in the facilities of the manufacturer, where the welding procedure and welding device were approved of by the relevant services.

Branches are formed in such a way that all connections are located on the main pipe, diameter DN50mm.

As much as it was possible, branches were designed in a way so that the diameter of the connection to the main ring was minimum DN50 i.e. Ø60.3mm. Since it was not possible, for places where pipelines less than DN50 mm were connected (for DN32 i DN25), it was envisaged that the connection on the main ring was formed by a piece of a pipe DN50 to which appropriate reduction would be welded (DN50/DN32 or DN50/DN25 depending on the fact whether a branch had one or two heads). Above requirements of EN12845 are satisfied in this way. All those branches have to be formed in a workshop, and then, final pieces are brought to the site, with already prepared connections DN50, that may be welded on the spot, that is, in the facility where the installation will occur.

Branches with connections for heads need to be prepared in workshops of the manufacturer’s buildings. Branches are welded for the ring and the welded pipes have to be labelled by a name or abbreviation of the contracting company at the distance of 100 mm from the ends. Labels must be legible and permanent as well as placed on the two opposite sides of the pipe circumference. Welded parts must comply with DIN EN 10 241. The hole for the welded part has to correspond at least to the outer diameter of the thread and has to be maximum 2mm less than the outer diameter of the socket. The hole shall have internal bevels. Welding process on the pipes with diameter ≤50 mm has to be accepted by the relevant service.

### MAIN DISTRIBUTION

Main distribution starts from the sprinkler valve.

This main pipeline and the ring for the entire facility is filled with water. After the fire, it is necessary to drain the rest of water away. That is why it is formed with a 5‰ incline. At those places there are drainage valves which open after the fire, and the pipeline is emptied. Afterwards, it is functional again. In order to prevent misuse of these valves, it is necessary to take off small wheels after closure, so as to avoid unauthorized operation.

### FLOW INDICATORS

In the facility, there are flow indicators envisaged and installed which give signals. Sensitivity of the indicators should be less than 50% of the head capacity, that is, less than 0.5l/s.

In case of fire, water will flow through the head. The flow will be indicated on the level indicator. Signal from the indicator arrives to the fire switchboard, so that there is confirmation of the fire occurrence.

Flow indicators are envisaged for every part and there are four of them in total. The indicators are set on the place of verticals separation in compliance with suggested distance from side pipelines and anything that may disturb regular work of indicators. On each branch, there is a valve which may separate ring under the ceiling of a certain level. Above flow indicators, there is a section for testing indicators work. Drainage is carried out in the drainage vertical which is not subject to this project and is further discussed in the project of water supply and sewage.

### 5.1.2. ESTIMATED BILL OF QUANTITIES

    - EQUIPMENT AND DEVICES

    - note: purchase, delivery and installation are necessary for entire equipment

    - WET ALARM SPRINKLER STATION set with valve DN150 PN10, retard chamber, pressure switch, alarm bell, impurity strainer, manometers, necessary taps, counter flanges, seals, screws, nuts and elastic washers. Total 1,0 set.

    - FLOW METER DN80 PN16 RANGING FROM 0-636m3/h, Set of flanges, counter flanges, seals, screws,nuts and washer. Тotal 1,0 set.

    - FLANGE STAINER set of counter flanges, seals, screws ,nuts and elastic washers, DN150 PN16. Тotal 1,0 set.

    - Backflow prevention device, with flanges, hydraulic,with attestation. It is calculated and paid per one installed piece, set of flanges, counter flanges, seals, screws,nuts and elastic washers. DN150 PN16. Тotal 1,0 set.

    - NON-RETURN CLAPPER INSTALLED BETWEEN FLANGES Set of flanges, counter flanges, seals, screws,nuts and elastic washers. DN150 PN16. Тotal 1,0 set.

    - Sluice valves with flange, SRPS M.C5.670 2A Set of  counter flanges, seals, screws,nuts and elastic washers, DN150 PN16. Тotal 8,0 sets and DN100 PN16. Тotal 3,0 sets.

    - Micro switch providing information on valve position (open/partially closed). Тotal 3,0 pcs.

    - Drainage valve: DN40 PN16, total 1,0 pcs and DN20 PN16, total 3,0 pcs

    - Drainage set: Galvanized pipes DN50, galvanized pipes DN25, galvanized fittings, hopper for sprinkler valve,hopper for alarm bell. Carried to the nearest drain. Total 1,0 set.

    - VALVE FOR TESTING AND DRAINAGE AT THE ENDS OF THE MAIN RINGS, DN50 PN16. Total 9,0 sets.

    - Manometer Ø100mm, with manometer type and compensation pipe R1/2",  ranging 0-16bar. Total 2,0 pcs.

    - Flow indicator with imerssion feather, shaft collar for fixing on the pipe, elektrocontacts and a regulation switch DN100 PN16. Total 4, sets

    - FLOW INDICATORS TESTING SET, K=80 set composed of nipples for testing with a factor K=30, ball valve 3/4" manometer ranging from 0-16bar 1/2" in accordance with VDS. Total 4,0 sets.

    - STEEL THREADED NIPPLE R1/2“ WITHOUT SEAM SRPS M.B6.306. Total 94 pcs.

    - SPRINKLER HEAD HANGING, type „QUICK RESPONSE“, 1/2”; K= 80, t=68°C. Total 94,0 pcs.

    - SPRINKLER HEAD HANGING, SPAREpart, type „QUICK RESPONSE“, 1/2”; K= 80, t=68°C. Total 24,0 pcs.

    - Cabinet for spare heads, Capacity12 sprinkler heads. Total 2,0 pcs.

    - KEY FOR HEADS ASSEMBLY G ½". Total 5,0 pcs.

    - Purchase, transport and installation of flexible chrome pipes  1/2" for connecting sprinkler and pipe network in a lowered ceiling . Average length of the connection is 60 cm. Flexible pipes for operating pressure 10 bars. At both ends, each connection has union flat joint  1/2" with thread, whereas in order to attach the sprinkler rosettes and heads to the lowered ceiling, there is a metal washer and a spring. Calculations per peace of connection. Total 94,0 pcs.

    - Purchase, transport and installation of a cabinet, made of stainless steel, with stable fire extinguishing couplings with caps, couplings type  "B" (2x2 1/2") with drain DN100. Callculation per set delivered and installed on the façade of the cabinet. Total 1,0 set

    - Electric heater with work and limit thermostat for temperature maintenance in the sprinkler station, capacity of 9KW. The heater has wall holder and all necessary equippment  for smooth and safe operation. Total 1,0 set.

PIPE NETWORK AND ARMATURE

    - Steel seamless pipes, according to SRPS EN 10220:2005 WITHOUT NIPPLES,  the following dimensions:

- DN150 (Ø165.1x4.5mm). Total 40,0m.

- DN100 (Ø114.3x3.6mm). Total 150,0m.

- DN50 (Ø60.3x2.9mm). Total 13,0m

- DN32 (Ø42.4x2.6mm). Total 35,0 m.

- DN25 (Ø33.7x2.6mm). Total  220,0 m.

- DN20 (Ø26.9x2.3mm). Total 12,0 m.

    - Cast steel fittings 90°, R=1.5D, SRPS M.B6.821, the following dimensions:

- DN150 (Ø165.1x4.5mm). Total 10,0 pcs.

- DN100 (Ø114.3x3.6mm). Total 15,0 pcs.

- DN50 (Ø60.3x2.9mm). Total 2,0 pcs.

- DN32 (Ø42.4x2.6mm). Total 1,0 pc.

- DN25 (Ø33.7x2.6mm). Total 2,0 pcs.

    - Purchase, transport and installation of a set of various steel  fittings, reduction, elbows, pipe tees, backings, hard points, flanges and all other elements for sprinkler network. Carriers are fixed for the reinforced concrete structure and steel construction. Price also includes steel rawl plugs, screws, rods and and clamps. Carriers capacity:

- pipes to DN50. Total 200 kg,

- pipes from DN50 to DN100. Total 350 kg,

- pipes from DN100 to DN150. Total 500 kg.

Calcullation per set 50% of previous 2 positions amount.

    - ADDITIONAL MATERIAL for welding, electordes, wire, welding gas, reducing pieces and the like. Total 1 lump sum.

    - Purchase, transport and installation of numerous steel holders  and carriers for sprinkler network pipes. Calculation per kg of carriers with external elements. Total 600,0 kg.

    - Cleaning pipes and backings from rust and dirt and double minimization of corrosion by  protective anti-corrosion paint. Total 130,0 m².

    - Painting pipes and backings with final paint (RAL 9001). Only visible parts of pipe network will be painted. Total 130,0 m².

PREPARATORY-FINAL WORKS

    - Development of instructions for operating and maintaining as well as submission to the investor. Total 1,0 set.

    - Developing as-built design and submission to the investor. The project will be developed in four copies, with all necessary certificates and decisions.

    - Testing a stable system for water spray and network, performing functional check of each zone separately. Minutes shall be took upon testing. It is necessary to submit certificates on technical and functional conditions of the equipment and materials incorporated.   Attestation has to be performed by the company verified for the activity, which owns appropriate liscence.

    - Posting notices and warning notes.

    - Other preparatory-final works with transport  of materials and tools, exploring the site and documentation, protecting the site and delivery of installation to the investor upon work completion.

5.2. SMOKE AND HEAT EXHAUST VENTILATION SYSTEM

5.2.1.TECHNICAL DESCRIPTION

Smoke exhaust is achieved by opening a smoke damper dimensions 1120 x 800 mm which is placed in a flue 1120 x 800 mm  and a centrifugal roof ventilator  to the outer atmosphere.

The centrifugal roof ventilator has the following features:

- L=18800 m³/h,

- Δp=50 Pa,

- N=2,2 kW,

- n=700 minˉ¹,

The smoke and heat exhaust ventilation system  is defined on the basis of:

- volume exhaust capacity

- pressure drop in the system

- velocity of flow in a duct

- position of a duct is determined on the basis of the need for efficient smoke and heat exhaust ventilation from inner space.

Features of the ventilator are such that it can work for two hours at the temperature of 400°C or permanently at the temperature of 200°C.

Activation of the smoke exhaust ventilator is possible manually or by a remote control.

Outside air passage or fresh air supply is controlled by the regulation electro drive dampers   1185 x 900 mm, placed on a north side of the building façade at a height of 800 mm from the auditorium ground.

A smoke damper is intended for opening of a flue ventilation duct, as a part of a flue system, which uses forced smoke exhaust from the fire space. In normal condition, the damper is closed, whereas it opens in case of fire.

Fire resistance of a smoke damper is 120 min in compliance with SRPS EN 12101-8, a trial according to SRPS U.J1.174, certificate of conformity (manufacturer’s declaration).

The smoke damper  1120 x 800, is composed of housing made of galvanized steel sheet, blade made of fire resistant material, electric actuator with return spring, and small embedded parts.

When the blade is closed, the electric actuator is constantly under voltage.

Loss of power opens a blade by a force of return spring, and with new position of electric actuator under voltage, the blade goes back to normal, closed position.  In the actuator there are contacts signalizing the blade position.

The smoke and heat exhaust ventilation system elements from the auditorium space has to meet the following criteria:

- roof ventilator, 400ºC, 120 min in compliance with SRPS EN 12101-3 standard, certificate of conformity (manufacturer’s declaration)

- a smoke damper: fire resistance of a smoke damper is 120 min in compliance with SRPS EN 12101-8, a trial according to SRPS U.J1.174, certificate of conformity (manufacturer’s declaration)

- smoke extraction ducts have to be examined according to the SRPS EN 1366-9 standard, report on examination.

System components are placed (supplied) on the market, only if the system complies with the prescribed technical requirements, if its conformity is assessed according to the prescribed procedure, and if it is marked in accordance with regulations and accompanied by signed certificates of conformity and other prescribed documents.

Manner of implementation of conformity assessment is closely determined by the Regulation on manner of conformity assessment, content of document of conformity, and shape, appearance and content of mark of conformity (Official Gazette of the RS no. 98/09).

As the smoke extraction ventilators are safety equipment, for power supply it is necessary to use safety cables N2XH-FE 180/E90, which are fire resistant with insulation integrity of 180 min and function integrity of 90 min (according to IEC 60331 standard), without halogen elements with low emission of smoke and toxic gasses.

Safety cables have to function in the fire regime and supply electric consumers of installation for smoke and heat exhaust and toxic combustion products for the time when the installations work in case of fire.

It is envisaged that the electrical circuit of the smoke exhaust system is separated from other electrical circuits, so that an electrical error or any other intervention in one system does not influence work of other systems.

In the auditorium, stable installation for water-based fire extinguishing (sprinkler installation) is envisaged, so it is necessary to regulate the smoke and heat exhaust ventilation system in a way that the fire extinguishing system is activated first (sprinkler installation) and then smoke and heat exhaust ventilation devices.

In case of fire and a need for smoke and heat exhaust ventilation, it is necessary to automatically activate a smoke exhaust ventilator, a smoke damper and regulation damper for fresh air supply. A button for manual installation will be installed on the accessible place (on a fire access road), whereas its position will be in charge of the electro project.

Remote and automatic activation devices will be in compliance with the appropriate regulations and laws, and represent the responsibility of the electro project

Electric power supply and smoke and heat exhaust ventilator control have to be reliable in case of fire. For the smooth operation of the mentioned system, the cable installation has to be set up either out of reach of fire or an appropriate class for the maintenance of functionality has to be envisaged. The control panel will be installed in a premise out of fire danger.

5.2.2. ESTIMATED BILL OF QUANTITIES

EQUIPMENT AND DEVICES

note: purchase, delivery and installation are necessary for entire equipment

    - Cetrifugal roof ventilator,  the features:

L=18800 m³/h,

Δp=50 Pa,

N=2,2 kW,

n=700 minˉ¹,

Declaration of the manufacturer according to  SRPS EN 12101-3 standard. Total 1,0 set.

    - Smoke damper, dimensions  1120 x 800 mm,  L=600 mm the following technical features::

- Housing PPK made of galvanized steel sheet , 1,50 mm  thick and flange thread  30 mm.

- Elctric actuator with return spring and end contacts,with cables 6x0,75 mm² and 2x0,75 m, length 1 m.

- Signalization of open and closed postition.

- Fire resistance120 min.

- Declaration of the manufacturer according toSRPS EN 12101-8 standard,

- Cable terminals from electric actuator driver  PPK made of fire resistant material.

Total 1,0 set.

    - Regulation electric drive damper dimensions 1185 x 900. Total 1,0 pc.

    - Smoke and heat exhaust ducts made of galvanized steel sheet 2mm thick. Method of installation, connecting duct parts and fittings, and manner of installing according to the technical conditions, a set of connectors and seals as well as supporting and hanging material according to SRPS EN 1366-9 standard. Weigth of channels, profiles, backing, sealss and screws.  Total 350 kg.

    - Final-preparatory works, testing and  trials regarding installation regulation.

5.3. HEATING, VENTILATION AND AIR CONDITIONING SYSTEM

5.3.1.TECHNICAL DESCRIPTION

A main element of the ventilation and air conditioning system is an air chamber

The air chamber DR+FB+HV+VU+DI+EG+IP was allowed.

Letter symbols of the parts:

DR-regulation damper

FB-coarse filter section

HV-cooler

VU-ventilator user

DI-diffuser

EG-electric heater

IP-output terminal

The air cabinet is equipped with all necessary equipment for automatic regulation and signalization, which provides the required parameters of air in the auditorium space.

When using the installation, instructions for control and maintenance provided by the deliverer of the equipment, must be followed.

In fire resistant ventilation ducts going through walls, fire resistant dampers are set.

The damper activation is thermal over melting thermal fuse, which is automatically activated by spring mechanism that closes the damper blade at the temperature of 70 ±2°C. Thermal activation circuit (easily melting) can be removed from the outside damper, which enables easy control of its correctness. Once used melting element has to be replaced, with a new one, repair is not allowed. On the housing of PPZ, end positions of handles for blade drive are marked OPEN and CLOSED.

Air is exhausted from the auditorium space through wall combined fixed dampers (2 pcs) dimensions 1185 x 900mm. Combined dampers are combination of fixed dampers FŽ with overpressure damper PŽ-T.   PŽ damper blades are opened by difference between pressure on one side and the other side of the damper by air flow through the damper in a given direction. After termination of the air flow, PŽ damper blades close and prevent air flow in the opposite direction. On the top of damper blades there is a sponge seal, which reduces noise during opening and closure of the dumper.

5.3.2. ESTIMATED BILL OF QUANTITIES

HEATERS

- Purchase, delivery and installation of heaters, with electronic thermostat, 
switch for on / off and connection cable length of 1.5 m and DIN plug.  Also with low temperature heaters and mount, with built-in protection IP 2,4 the following characteristic:

- Power: 400 W. Total 5 units.

- Power: 600 W. Total 5 units.

- Power: 800 W. Total 3 units.

- Power: 1000 W. Total 3 units.

- Power: 1250 W. Total 7 units.

- Power: 1500 W. Total 2 units.

- Power: 2000 W. Total 4 units.

- Power: 500 W. Total 3 units.

- Power: 750 W. Total 3 units.

EQUIPMENT FOR AIR PREPARATION AND DISTRIBUTION

- Purchase, delivery and installation of the air chamber, consisting of the following elements:

- Revolutions per minute of electric motor n=1355 mm-1

- Power of electrical motor P=1.5 kW

- Available head  H=575 Pa

- Air flow rate V= 4000 m3/h

DR-regulation damper

FB-coarse filter section

HV-cooler

VU-ventilator user

DI-diffuser

EG-electric heater

IP-output terminal

Additional equipment for automatic control.

Total 1,0 set.

- Purchase, delivery and installation of the alluminium vent dampers, a set with a flow regulator for air insertion, dimensions: 930 x 620 mm. Total 1,0 set.

- Purchase, delivery and installation of  elastic jute strings or similar for installation between ducts and air chamber , dimensions: 910 x 630 x 300 mm. Total 2,0 sets.

- Design and installation of  ventilation ducts for insertion and extraction of air. Ducts will be made of galvanized sheet, thickness according to the technical regulations for such works. Calculation is carried out per kg of the installed material,  where carriers, holders, flanges, connectros and seals are included. The price includes minimazing and painting flanges and duct supporting and hanging elements with previous corrosion removal.

- Purchase, delivery and installation of  ceiling diffusers. Total 2,0 pcs.

- Purchase, delivery and installation of  overpressure ventilation dampers, dimensions 1185 x 900mm. Total 2,0 pcs.

- Purchase, delivery and installation of  fire resistant damper with thermal, manual and remote activation with solenoid, dimensions:

- 500 x 500mm. Total 1,0 pc

- 630 x 630mm. Total 1,0 pc

FINAL PREPARATORY WORKS

- Final preparatory works include:

- project analysis before works commencement;

- digging in walls;

- internal transport;

- contact with the supervising authority;

- testing installation on a hydraulic pressure;

- installation regulation and activation;

- collecting attesting documents and other administration activities, 5% of all above mentioned works is paid.

5.4. ELECTRICAL WORKS FOR THE ELECTRICAL INSTALLATION OF STAGE LIGHTING

5.4.1.TECHNICAL DESCRIPTION

Sta da pisem

5.4.2. ESTIMATED BILL OF QUANTITIES

STAGE LIGHTING SYSTEM

Stage spotlights

- Delivery and installation of the complete frensel lens spotlight (textured), wide, adjustable beam of "soft" light with edges in range from 130 to 590 made of extruded aluminium. Within the spotlight, one halogen light source is installed, rated power of 1.0 kW, rated voltage 230V/50 Hz, temperature  3200 ºK and light bulb base GX9.5. There is also a set of additional equipment: a protective lens net, a metal frame for filters, a four sided clapper, a  threaded silicone cable  3 x 1.5 mm2 minimal length 2.0 m with CEE connector, a hanging hook on pipes Ø 65 mm and a safety cable. Total 3,0 pcs.

- Delivery and installation of the complete spotlight with plano-convex fully transparent collecting lens, wide, adjustable beam of "hard" light, with very prominent edges in range of  100 to 650  made of extruded aluminium. Within the spotlight, one halogen light source is installed, rated power of 1.0 kW, rated voltage 230V/50 Hz, temperature  3200 ºK and light bulb base GX9.5. There is also a set of additional equipment: protective lens net, metal frame for filters, threaded silicone cable  3 x 1.5 mm2 minimal length 2.0 m with CEE connector, hanging hook on pipes Ø 65 mm and a safety cable. Total 2,0 pcs.

- Delivery and installation of the complete frensel lens spotlight (textured), wide, adjustable beam of "soft" light with edges in range from 120 to 610 made of extruded aluminium. Within the spotlight, one halogen light source is installed, rated power of 2.0 kW, rated voltage 230V/50 Hz, temperature  3200 ºK and light bulb base GX16. There is also a set of additional equipment: a protective lens net, a metal frame for filters, a four sided clapper, a  threaded silicone cable  3 x 1.5 mm2 minimal length 2.0 m with CEE connector, a hanging hook on pipes Ø 65 mm and a safety cable. Total 2,0 pcs.

- Delivery and installation of the complete spotlight with plano-convex  lens, wide, adjustable beam of "hard" light, in range of  50 to 650  made of extruded aluminium. Within the spotlight, one halogen light source is installed, rated power of 2.0 kW, rated voltage 230V/50 Hz, temperature  3200 ºK and light bulb base GX16.   There is also a set of additional equipment: protective lens net, metal frame for filters, four sided clapper, threaded silicone cable  3 x 1.5 mm2 minimal length 2.0 m with CEE connector, hanging hook on pipes Ø 65 mm and a safety cable. Total 7,0 pcs.

- Delivery and installation by collecting complete, wide beam, diffuse, asymetric spotlights of "soft" light, wide beam for stage lighting, equpped with a protective net, and a four-sided frame for glass filters, CAD/PF/ACV with a hook A20 and a safety cable, with halogen light source, rated power 1.0 kW, rated voltage 230V, 50 Hz, temperature 3200 K, with the base R7S and a thread silicone cable 3 x 2.5 mm2 length of l=2.0m. Total 4,0 pcs.

Regulation of stage lighting

- Delivery and installation of a manual table for regulation of stage lighting. Features:

- 24 channels of configuration with 24 regulators configurated as channels, submaster or playback

- MIDI IN/OUT connector

- 2 DMX512/1990 terminal on XLR-5F connector

- power supply 90-260V, 47/63Hz with automatic detection

Total 1,0 pc.

- Delivery and installation of a digital dimmer unit for installation of the  Rack

The output power of the dimmer unit is  6x3 kW with DMX512/1990 input over a connector XLR5 with galvanic insullation. On the front panel of the dimmer, there is a keypad with  LED display for programming and quick access to all functions, with a possibility of adjusting 10 dimmer curves, which can be individually selected for each dimmer cable, with constant storage of all programmed data. Dimmer power supply is 230V/400V,star, 3NPE (TN-S), 50/60 Hz. Within the dimmer, there is a low-noise ventilator for efficient cooling, controlled by a microproccesor with automatic stop of the ventilator and automatic protection from excessive temperature and gradual reduction of the dimmer exit to the output.  Individual protection of each dimmer MCB/1P (standard), protection of circuit 400V voltage. Total 1,0 pc.

- Training and certificates

- Certificates for the delivered equipment ,

- Manual for operation and maintenance of the stage lighting equipment,

- Training of beneficiaries.

Total 1 set.

Electrical installations of stage lighting system

- Perforated cable trays are delivered and installed plasticized in black matte colour, with set of caps and necessary installation tools:

- PNK200. Total 4,0 m.

- PNK100. Total 12,0 m.

- PNK50. Total 12,0 m.

- Delivery and installation of cables intended for power supply of the stage lighting system. Cables are placed in cable trays:

N2XH-J 3x2,5mm². Total 468,0m.

LIHCH 2x0,5mm². Total 50,0 m.

- Delivery and installation of industrial wall sockets 16A 3p with visibly a marked dimmer number.  Sockets are installed on the wall at the side spotlight carriers.Total 19,0 sets.

- MDC of stage lighting. Total 1,0 set.

- Testing stage lighting installations, issuing appropriate certificates and delivery of certificates for entire electrical equipment installed. Total lump sum.

STAGE MECHANICS SYSTEM

Stage mechanics devices

- Delivery and installation of the following stage mechanics elements:

EMRC - Motorized light hoist

Features of motorized light hoist with mobile drive train:

* load capacity: 150kg

* length and type of support: 5,5m, Al "Ω" profil

* working stroke: 6m

* speed: 0,09m/s

* drive train: 0,75kW

* pivot point: 4

* number of trolleys with brakes: 5kom

* number and type of connector: 5x16A dim

* number and type of connector: 1 set XLR5pin m/f

* related electrical installations: set

* cable tray: segmented Al pantograph

* additional locksmith structures: console, racks ...

Total 1,0 pc.

BNR - Spotlight side girder

Features

* length and type: pipe Ø48mm, L=1,5m

* spotlight girder "lakat"

Total 2,0 pcs.

HNR - spotlight horizontal girder

Features

* length and type: pipeØ48mm, L=8m

Total 2,0 pcs.

- Training and certificates

- certificates for the delivered equipment ,

- Manual for operation and maintenance of the stage mechanics equipment,

- training of beneficiaries.

Total 1,0 set.

Electrical installation of the stage mechanics system

- RO-SM Stage mechanics distribution cabinet

RO-SM in intended for providing power and controlling with one electric motor drive of the stage mechnics and is located in the appropriate place above the audience. The cabinet is a product by a stage mechanics devices manufacturer, which contains complete equipment neccesary for supply, protection and management of electric motor drive. Total 1,0 set.

- Cables

Delivery and installation of cables intended for power supply of the stage mechanics system. Cables are placed in cable trays:

* cable N2XH-J 5x1,5mm². Total 50,0 m.

* cable N2XK 4x25mm². Total 25,0 m.

* cable N2XK-J 1x16mm². Total 25,0 m.

* cable N2XH-J 5x2,5mm². Total 20,0 m.

- Certificates and testing electrical installations

Testing stage mechanics installations, issuing appropriate certificates and delivery of certificates for entire electrical equipment installed.  Total 1 set.

- As-built project

Development and delivery of as-built project for the stage lighting and mechanics. Total 1,0 set.

AUTOMATIC FIRE PROTECTION CURTAIN

Fire protection curtain with necessary control panel and related equipment

- Delivery and installation of the fire protection curtain elements and necessary automatics:

Fire protection curtain is fire resistant 90-120 min. It is made of fibre glass fabrics, especially tested for fire resistance- it holds fire up to 1100 °C for 90-120 minutes.

Threaded plate is 70mm thick and made of galvanized steel. Vertical pipes are galvanized 110 mm wide.

Speed of curtain closure is 7m/min. Upon fire occurrence, the curtain is automatically closed, even with supply interruption, thus activating optic and sound alarm.

On the lower part of the curtain, there is additional contact safety rubber.

Dimensions of a panel 300x250mm and it enables all door functions up to 4 hours after power outage. On the panel, there is the command UP-STOP-DOWN button integrated.

Power supply of the curtain is 220/230V/50 X3/20 A. Electrical connector 3 x 2,5mm.

The curtain dimensions are 11250mm x 4500mm.

The fire resistant curtain has to be delivered with appropriate certificates from the manufacturer.

Total 1,0 pc.